## Administrative
Location | Site Name | JBSA-Kelly Field Annex
| RPSUID | 2334
| DLA Site Code | KEQ
| Hours of Operation | 24 Hours of Operation
| Address | 102 Hall Boulevard, San Antonio, TX 78236
Contract | Contractor
Contract #
Local POCs | QAE Name
QAE Phone
QAE Email
Alt QAE Name
Alt QAE Phone
Alt QAE Email
DLA/SCP POCs | DLA PM Name
DLA PM Phone
DLA PM Email
SCP PM Name
SCP PM Phone
SCP PM Email
Contractor POCs | Contractor PM Name
Contractor PM Phone
Contractor PM Email
Contractor QC Name
Contractor QC Phone
Contractor QC Email
Contractor SM Name
Contractor SM Phone
Contractor SM Email
USACE POCs | USACE PM/COR Name
USACE PM/COR Phone
USACE PM/COR Email
USACE PE Name
USACE PE Phone
USACE PE Email
USACE KO Name
USACE KO Phone
USACE KO Email
Instructions:
This table shows the minimum information required. Additional details should be included based on site specific requirements. Additional POCs may be required.

## General Facility Description
Facility Description
Purpose: This Facility Maintenance Plan provides guidance for Contractor personnel in the operation, inspection, and maintenance of permanently installed fuel facilities operated under the control of the Quality Assurance Evaluators. Federal, state, and local environmental laws and regulations shall be complied with if this plan is in conflict with them. Scope: The instructions prescribed by this plan outline general fuels maintenance information associated with fuel storage and dispensing systems and provides the minimum periodic contractor maintenance and inspection criteria requirements for the systems. This plan is to be used in conjunction with other existing directives governing fuel system operations and maintenance requirements. Conotractor will properly maintain and repair federally funded petroleum systems and facilities in order to provide compliance with applicable code, criteria, and federal, state, local and/or host nation regulations. Fuels Facilities: Organizational tanks, and associated dispensing equipment are maintained and operated by the owning organization. Fuel system maintenance contractors shall perform all maintenance and associated procurement actions on installed fuel systems. Each installation under the Southwest Division contract are military land-based facilities who receive, store, distribute, and/or dispense liquid fuels. Standard fuel system equipment includes: a) Above Ground Sorage Stanks (AST), Underground Storage Tanks (UST) b) Filter/separator and other filtration device maintenance access, particularly element removal. c) Manual valves d) Meter Registers, and Flow Meters. e) Control Valves. f) Pumps g) Tank Monitoring Equipment and Instruments h) Alarms i) Fire Fighting Equipment Site Specific General Information:
Instructions:
Include a general facility overview and description of each fuel system for the sites in accordance with UFC 3-460-01. Examples include: Bulk Storage Facilities, Aircraft Fueling Facilities, Marine and Dispensing Facilities, Ground Products Fueling Facilities, Alternate POL Facilities, and Support Facilities. Also include facility #s, facility names, fuel type, photos, and any other pertinent information.
Include Site Specific Conditions and Restrictions in this tab.

## Communication Plan
Instructions:
Communication plan shall address in/out briefs, lines of communication, coordination for access, etc.

## Safety
Instructions:
Site Specific Addendum and Activity Hazard Analysis, which are Attachments to the APP, specific to activities or tasks related to recurring maintenance for this site.

## RM Schedule
Instructions:
Link RM schedule here

## Task Matrix
Applicable Facility Assets | [9 empty] | UFC System Level Maintenance Frequency |  |  |  | Special Considerations
Real Property Unique Identifier (RPUID) | Real Property Facility # | Real Property Facility Name | Operational Area | Component Type | Base Asset ID | Component Unique Identifier (CUID) | Make | Model | Capacity/Size | Q | S | A | UFC Section Reference | Additional Manufacturer RM Requirements | Operator/ equipment Requirements | System availability | Other Contract | Comments
| 980 | Operations Building / General Facility | Operations Building | Signage and Markings | Bldg 980 OPs bldg entire bulk area fencing |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 980 | Operations Building / General Facility | Operations Building | Signage and Markings | Bldg 980 fencing signage |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Canopies | Issue Pad Canopy |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Emergency Eyewash/Showers | Issue Pad |  | Guardian | Not Listed | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Automatic Air Vents | Issue Line 3 Separator Air Eliminator |  | Armstrong | 11AV | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Automatic Air Vents | Product Saver |  | The Protectoseal | 6672 | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Automatic Air Vents | Issue Pump 2 Separator Air Eliminator Tank |  | Armstrong | 11AV | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Automatic Air Vents | Issue Pump 1 Separator 1 |  | Armstrong | 11AV | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Automatic Air Vents | Receipt Filter Separator Air Eliminator |  | Armstrong | 11AV | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Receipt Separator |  | Facet | VCS-1243-436 | 1,200 GPM GPM/SCFM 100 Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Issue Pump 2 Filter Separator |  | Facet | VCD-643-236 | 600 GPM GPM/SCFM 100 Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Issue Pump 1 Separator 1 |  | Facet | VCS-643-236 | 600 GPM GPM/SCFM Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Issue line 3 separator |  | Facet | VOS-643-256 | 600 GPM GPM/SCFM Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Basket Strainers | Issue Pump 2 Basket Strainer |  | Titan | Titan 8-WCB 150 | 8.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Basket Strainers | Issue Pump 1 Basket Strainer |  | Titan | 8-150 | 8.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact |  | With DP Gauge
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Basket Strainers | Issue Pump 3 basket strainer |  | Titan | 8 150 WCB | 8.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Vertical Inline Pumps | Issue line 3 pump |  | SPX Clyde Union Pumps | C130 | 600 GPM GPM/SCFM | X | X | X | 3-8.1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Vertical Inline Pumps | Issue Pump 1 |  | SPX Clyde Union Pumps | 800 C0245354X | 600 GPM GPM/SCFM | X | X | X | 3-8.1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Vertical Inline Pumps | Issue Pump 2 Pump |  | SPX Clyde Union Pumps | 800C02453AX-WGB | 600 GPM GPM/SCFM | X | X | X | 3-8.1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Vertical Inline Pumps | Product Saver |  | Goulds | 1SV5NA3A30-M01 | 10 GPM GPM/SCFM | X | X | X | 3-8.1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Refuel Control Valves | Check Stand |  | Cla-Val | 1000 MM | 4.0 in. | X | X | 0 | 4-3.2.5 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Non-Surge Check Valves | Issue line 3 non surge check valve |  | Cla-Val | 150/PN16 | 4.0 in. | X | X | 0 | 4-4.2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Non-Surge Check Valves | Issue Pump 1 Non-Surge Check Valve A10 |  | Cla-Val | 4-150 | 4.0 in. | X | X | 0 | 4-4.2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Non-Surge Check Valves | Issue Pump 2 Non Surge Check Valve A10 |  | Cla-Val | 150/PN16 | 4.0 in. | X | X | 0 | 4-4.2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separator Control Valves | Issue line 3 separator control valve |  | Cla-Val | 150/PN16 | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separator Control Valves | Issue Pump 1 Separator 1 Filter Separator Control Valve |  | Cla-Val | CF8M | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separator Control Valves | Receipt filter separator control valve |  | Cla-Val | 150/pn16 | 8.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separator Control Valves | Issue Pump 2 Separator Control Valve A9 |  | Cla-Val | 150/PN16 | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Defuel/Flush Valves | Type III defuel flush valve |  | Cla-Val | Mil flow 150 | 8.0 in. | X | X | 0 | 4-4.2.3 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Back Pressure Control Valves | BPCV |  | Cla-Val | 50 MM | 2.0 in. | X | X | 0 | 4-4.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Issue line 3 CRD |  | Cla-Val | 9803803H | 0.375 (3/8) in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Issue line 3 pv |  | Cla-Val | 47088A | 0.375 (3/8) in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Hydrant Test Stand/Flush Station Pressure Control Valve on DB&B Valve O-36-NC |  | Cla-Val | 20-200 | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Hydrant Test Stand/Flush Station |  | Cla-Val | Not Legible | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | South Fillstand |  | Cla-Val | 2106612K | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Issue line 3 CRL |  | Cla-Val | 76154F | 0.375 (3/8) in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Hydrant Return Loop Pressure Control Valve |  | Cla-Val | 6-150 | 6.0 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Hydrant Loop Issue DBBV |  | Cla-Val | 8106602K | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Hydrant Loop Return |  | Cla-Val | 006602K | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | North Fillstand |  | Cla-Val | 106602K | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Control Valves | Test Stand Return DBBV |  | Cla-Val | Not Legible | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Hydrant Adapters | Check Stand |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Surge Suppressors | Check stand surge arrestor #2 |  | Young Engineering | 40BSA-27 | N/A | X | X | 0 | 4-7.5 | No Additional Manufacturer Requirements | Operator required for system operation | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Surge Suppressors | Surge Suppressor 1 |  | Young Engineering | 40BSA-27 | N/A | X | X | 0 | 4-7.5 | No Additional Manufacturer Requirements | Operator required for system operation | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Issue line 3 Pump Piping |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Issue line 3 separator piping |  | N/A | N/A | 6.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Outside of dike bldg 981 piping |  | N/A | N/A | 8.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Issue line 2 piping |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Issue line 1 piping |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant issue piping |  | N/A | N/A | 12.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant issue piping |  | N/A | N/A | 10.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant receipt piping |  | N/A | N/A | 8.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant receipt piping |  | N/A | N/A | 10.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant receipt piping |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant receipt piping |  | N/A | N/A | 6.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Hydrant receipt piping |  | N/A | N/A | 8.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Bldg 981 issue piping |  | N/A | N/A | 8.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Bldg 981 piping |  | N/A | N/A | 2.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Aboveground Piping | Bldg 981 piping |  | N/A | N/A | 1.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Sight Flow Indicators | Issue line 3 separator sight glass |  | Kenco | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Sight Flow Indicators | Issue Pump 1 Separator 1 Sight Glass |  | Kenco | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Sight Flow Indicators | Issue Pump 2 F/S Sight Gauge |  | Kenco | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Sight Flow Indicators | Receipt filter separator sight glass |  | Kenco | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Sight Flow Indicators | PRT sight glass |  | Kenco | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Gate Valves | Bowser Dike Drain (PIV) |  | Mueller | A20806 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 DP Gauge Inlet |  | Gammon Tech Products | GTP-1149 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 DP Gauge Outlet |  | Gammon Tech Products | GTP-1149 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Test Stand Return PCV Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | South Side Fillstand Low Point Drain |  | Apollo | Not Labeled | 1.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | South Side PRV Line Drain M 207 NC |  | Flow-Tek | RF15 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue line 3 Downstream Control Valve |  | Flo-Tite | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue line 3 Post Control Valve |  | Flo-Tite | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Isolation 89 NO |  | Flo-Tite | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Defuel Flush Line Ball Valve 2 |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Line |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Line Drain |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Line |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT drain Line |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 1 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 2 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 3 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 4 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Isolation |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Isolation |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 5 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 6 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 7 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | DPT Drain 8 |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Defuel Flush Line Ball Valve, Downstream defuel valve |  | Flow-Tek | CF8M | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | BPCV Line Isolation O-45-NO |  | Flow-Tek | CF8M | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | BPCV Gauge Isolation |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | BPCV High Point Drain |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | BPCVO-44-NO |  | Flow-Tek | CF8M | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Defuel Flush Line Ball Valve 1 |  | Flow-Tek | CF8M | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Check Stand Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Check Stand SPR Isolation 2 O-32-NC |  | TCI | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Check Stand Isolation 0-33-NC |  | TCI | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | BPCV Blind Flange M-233-NC |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue line 3 check valve |  | Flo-Tite | Rf15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue line 3 check valve |  | Flo-Tite | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue line 3 at Separator |  | Flo-Tite | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Sample Cock |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S Drain 1 |  | Flo-Tite | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S PRV Test Tee |  | Gammon Tech Products | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Sample Cock |  | Schultz | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S DP Gauge Inlet |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S DP Gauge Outlet |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Control Valve PCV Isolation |  | Cla-Val | Not Labeled | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Line Pressure Relief Isolation Valve M-240-NO |  | Flo-Tite | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line Drain Valve M-131 NC |  | Flo-Tite | Sf150 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S Air Eliminator Isolation Drain |  | Flo-Tite | T12SS | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 F/S Inlet Ball Valve Sample Port |  | Gammon Tech Products | 1000W08 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Sample Valve |  | Gammon Tech Products | GTP-992-4MS | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Pressure Relief Sampling Ball Valve |  | Gammon Tech Products | 1000-WOG | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Sample Cock |  | Gammon Tech Products | Gtp-9924MD | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Outlet Sampling Valve Port |  | Gammon Tech Products | 1000 WOG | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Air Eliminator Drain |  | Flo-Tite | RF15 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Air Eliminator Isolation |  | Flo-Tite | RF15 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Drain Line Isolation |  | Flo-Tite | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Drain Line Isolation |  | Flo-Tite | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt filter separator drain valve |  | Flo-Tite | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line PRV Isolation M-160-NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Surge Suppressor 1 Sampling Port |  | Flo-Tite | RF15 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Issue Line Pressure Relief Isolation Valve M-172-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Main Issue Line from Tanks Drain Valve M-112-NC |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Basket Strainer Drain |  | Flo-Tite | Cf8m | 1.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 DP Gauge Inlet |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 DP Gauge Outlet |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Inlet Valve for DP Gauge on Basket Strainer |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Outlet Valve for DP Gauge on Basket Strainer |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Isolation Valve M-117-NC |  | Flo-Tite | F150 | 1.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Pressure Gauge Isolation Valve M-118-N0 |  | Flo-Tite | F150 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Pressure Relief Valve before PRV M-125-NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Isolation valve after PRV |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Pressure Gauge Isolation Valve M-127-N0 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Pressure Gauge Isolation Valve M-127-N0 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S Air Eliminator Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Filter Separator 1 Sample Port |  | Schults | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Sump Ball Valve M-146-NC |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator DP Gauge Inlet Ball Valve |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator DP Gauge Outlet Ball Valve |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Drain Line Isolation Valve M-145-NC |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Drain Valve |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Pressure Relief IsolationValve before PRV |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Pressure Relief Draw Off Valve |  | Flo-Tite | T12SS | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator PRV Outlet Valve |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Air Eliminator Outlet Valve |  | Flo-Tite | F150 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 PRV Outlet Isolation Valve M-152-N0 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Outlet Sample Port |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line High Point Valve |  | Conbraco | 2000WOG | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Isolation Valve O-40-NO |  | Flow-Tek | FTG22 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Test Stand/Flush Station Pressure Relief Isolation Valve M-187-NO |  | Not Labeled | Not Labeled | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Test Stand/Flush Station Pressure Relief Isolation Valve M-188-NO |  | Not Labeled | Not Labeled | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Line PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Line Sample Cock |  | Schultz | ANSI 150 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Line Sample Cock |  | Schultz | Sc-2051-1 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Line PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Line Isolation |  | Flow-Tek | 130007-11202533 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Bypass Line PRV Isolation |  | Flow-Tek | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt F/S Bypass Line PRV Isolation |  | Flow-Tek | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Main Issue Line PRV Isolation |  | Flo-Tite | 0035YS | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Main Issue Line Pressure Relief Line Isolation |  | Flo-Tite | F-150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Isolation |  | Flo-Tite | RF15 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tag 0-65-no
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 High Point |  | Flo-Tite | 0035YS | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Gauge Isolation |  | Flo-Tite | 0035 YS | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Pump Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Gauge Isolation |  | Flow-Tek | F15 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Pressure Relief Line |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Main Line Drain |  | Flo-Tite | 0035YS | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S PRV Isolation |  | Flo-Tite | 0035 YS/ F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S PRV Discharge |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 F/S Pressure Relief Line |  | Flo-Tite | 0035 YS/F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue ump 3 F/S Drain 2 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 3 Downstream Control Valve PRV Line |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Ball Valve 0-73-N0 |  | Flow-Tek | 8-150 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Basket Strainer Drain Valve M-116-NC |  | Flo-Tite | 1 1/2-150 | 1.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | South Side PRV Isolation 1 |  | Flow-Tek | RF15-2 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | South Side PRV Isolation 2 M 206 NC |  | Flo-Tite | SF150 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | South Fillstand |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | North Fillstand PCV Isolation |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Return DBBV |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Issue PCV Isolation |  | Flo-Tite | T12SS | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Issue PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Issue PRV Discharge M-173 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Isolation Valve for Pressure Relief Line M-123-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line FS Slow Fill |  | Flow-Tek | 8-150 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Ball Valve 71 |  | Flo-Tite | RF-15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 F/S Inlet Ball Valve 70 |  | Flo-Tite | RF-15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PRT Pump Discharge M-156 NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PRT Drain M-157 NC |  | Flo-Tite | SF150 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PRT Fill Isolation M142 NO |  | Flo-Tite | SF150 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PRT Return to Hydrant Loop M-049 NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Return Drain M-237 NC |  | Flo-Tite | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt Bypass 0-90-NO |  | Flow-Tek | FTG 30 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Return PRV M-050-NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return / Receipt |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 PRV inlet Isolation Valve M-151-N0 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Outlet Isolation Pressure Relief Valve M-150-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 2 Separator Outlet Ball Valve 66 |  | Flo-Tite | RF-15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return/Receipt Offload Valve O-DNC |  | Flow-Tek | RF15-WCB | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return / Receipt Drain Near Separator Inlet |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return/Receipt Offload Manifold Valve O-C-NC |  | Flow-Tek | RF15-WCB | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return/Receipt Offload Manifold Valve O-B-NC |  | Flow-Tek | RF15-WCB | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return/Receipt Offload Manifold Valve O-A-NC |  | Flow-Tek | RF15-WCB | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return Loop PRV Isolation M-236-NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue/Defuel Crossover Valve 0-38-NC |  | Flow-Tek | RF15 | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line M-159-NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Loop Pressure Gauge Isolation Valve M-232-NO |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Loop Valve M-40-NO |  | Flow-Tek | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Surge arrestor 2 sampling port |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Surge arrestor 2 ball valve |  | Flo-Tite | F150 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant return loop ball valve |  | Flow-Tek | F15 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant return loop |  | Flow-Tek | F15 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Surge Suppressor 1 Isolation Valve M-248-NO |  | Flo-Tite | F150 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return Line PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return Line PRV Isolation Discharge M-215-NO |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Issue Line Pressure Relief Isolation Valve M-173-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | SPR 1 Isolation |  | TCI | 4-150 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PIT Drain |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PIT Drain Line |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | PIT Isolation |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Test Stand/Flush Station Inlet Valve O-37-NC |  | Apollo | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Loop Drain Valve |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Loop Drain Valve |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Loop Pressure Gauge Isolation Valve M-231-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt Offload Line Pressure Relief Isolation Valve M-063-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt Line Drain Valve M-062-N0 |  | Conbraco | Unk | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt Offload Pressure Relief Isolation Valve M-064-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return Loop |  | GTP | GTP-1149 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return Loop PRV Isolation M-235-NO |  | Velan | ANSI 150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Issue Blind Flange O-56-NC |  | KV | Not Labeled | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return Line Isolation Valve M-241-NO for Pressure Relief Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Return/Receipt Offload Manifold Drain Valve M-242-NO |  | Apollo | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line High Point |  | Not Legible | Not Legible | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return / Receipt |  | Keystone | K lok Valve | 3.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Issue Valve O-74-NO |  | Flo-Tite | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Pressure Relief Inlet Isolation Valve M-149-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Outlet Isolation Valve for AE |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Hydrant Loop Return Sample Cock |  | Schultz | 816 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Receipt / Hydrant Loop Return O-84-NO |  | Flo-Tite | RF15 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Isolation Drain Valve M-XXX-NC on AE |  | Flo-Tite | CF8M | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Inlet Isolation Valve M-XXX-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Isolation Valve M-XXX-NO |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Isolation Drain Valve M-142-NC |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Isolation Drain Valve M-143-NC |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Separator 1 Isolation Drain Valve M-144-NC |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Inlet Valve O-78-NO on Filter Separator 1 |  | Flo-Tite | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Valve O-79-NO |  | Flo-Tite | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Line Pump Blind Flange |  | Keystone | 362-115 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Isolation Valve M-124-NO for Pressure Gauge |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Isolation Valve M-122 on Pressure Relief Line |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Isolation Valve M-116-NO for Pressure Gauge |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Isolation Valve M-114-NC |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | North Side Fillstand Low Point Drain |  | Apollo | Not Labeled | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Basket Strainer Drain Valve M-113-NC |  | Flo-Tite | CF8M | 1.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Return Line Drain |  | Flo-Tite | SF150 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Ball Valves | Issue Pump 1 Ball Valve O-81-NO |  | Flow-Tek | 8-150 | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Test Stand Return |  | Franklin Valve | 50 | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | South Side Fillstand |  | Franklin Valve | 711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | North Fillstand |  | Franklin Valve | 711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Hydrant Loop Return |  | Franklin Valve | D711 | 12.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Hydrant Loop Issue |  | Franklin Valve | D711 | 12.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Hydrant Loop Return O-82 NO |  | Franklin Valve | D711 | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Hydrant Test Stand/Flush Station Valve O-35-NC |  | Duraseal | 711 | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Hydrant Test Stand/Flush Station Valve O-36-NC |  | Duraseal | D711 | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Double Block and Bleed Valves | Receipt / Return Line 0-86-NO |  | Tru-Seal | 2T 203 | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Issue Pump 2 Separator Lower Sight Gauge Valve |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Issue Pump 2 Separator Upper Sight Gauge Valve |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Separator 2E sight Glass Upper |  | Kenco | HT0007 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Separator 2C Sight Glass Upper |  | Kenco | HT0007 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Separator 2C Sight Glass Lower |  | Kenco | HT0007 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Surge Suppressor 2 globe valve |  | Apollo | CF8M | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Surge Suppressor 1 Bypass Isolation Valve |  | Apollo | CF8M | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Separator 2E Sight Glass Lower |  | Kenco | HT0007 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Receipt Separator Sight Glass Lower |  | Kenco | HT0007 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | Receipt Sight Glass Upper |  | Kenco | HT0007 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | PRT Sight Glass Lower |  | Kenco | F316 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Globe Valves | PRT Sight Glass Upper |  | Kenco | F316 | 0.25 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Hydrant Return/Receipt Offload Manifold Check Valve on Pressure Relief Line |  | Not Labeled | Not Labeled | 1.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Receipt F/S Line |  | OIC | 8-150 | 8.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Surge Supressor 2 Check Valve |  | Titan | Cv42L | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Surge Supressor 1 Check Valve |  | Titan | CV42 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Hydrant Loop Return |  | OIC | 8-150 | 8.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | PRT Fill Line |  | Williams | Code 2766 | 2.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | PRT Discharge |  | Williams | Code 2861 | 1.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Issue Pump 2 outlet Check Valve |  | Titan 4-150 | CV42 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Issue Pump 1 Check Valve |  | Titan | CV42 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Check Valves | Issue line 3 check valve |  | Titan | CV42SS | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A25 Issue Pump 2 PRV |  | Taylor | T-7700-1 | 1.0 in. 30 - 500 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A24 Issue Line 3 Post Separator PRV |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A26 Issue Pump 2 Separator Pressure Reducing Valve |  | Taylor | T-8200-1 | 1.0 in. 226 - 450 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A35 Receipt filter separator prv |  | Taylor | T-8200-1 | 1.0 in. 226 - 450 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A27 Issue Pump 2 Separator Outlet PRV |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A37 Receipt filter separator control valve prv |  | Taylor | T-5200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A22 Issue line 3 PRV |  | Taylor | T-7700-1 | 1.0 in. 30 - 500 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A28 Issue Pump 1 Pressure Relief Valve |  | Taylor | T-7700-1 | 1.0 in. 30 - 500 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A34 Hydrant Loop Return |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A23 Issue Line 3 Separator PRV |  | Taylor | T-8200-1 | 1.0 in. 226 - 450 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A29 Issue Pump 1 Separator 1 Top Pressure Relief Valve |  | Taylor | T-8200-1 | 1.0 in. 226 - 450 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A36 Receipt / Return Line |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A30 Issue Pump 1 Separator 1 Pressure Relief |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A21 Return Loop |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A33 Receipt Offload Line Pressure Relief Valve |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A32 Hydrant Return Line Pressure Relief Valve |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A20 Issue Line |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A15 Hydrant Test Stand/Flush Station Pressure Relief Valve |  | Taylor | T-7700-3/4 | 0.75 in. 30 - 500 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A31 Main issue line |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A19 Return Line |  | Taylor | T-8220-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Thermal and/or Pressure Relief Valves | A18 Hydrant Issue Line Pressure Relief Valve |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 3 DP Pressure Gauge |  | Wika | Not Labeled | 0.25 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 2 Outlet Pressure Gauge |  | Ashcroft | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 2 DP Pressure Gauge |  | Wika | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Surge Suppressor 1 Pressure Gauge |  | Valley Instruments | Not Labeled | 0.25 in. 0 - 600 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue line 3 gauge |  | Ashcroft | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 1 Pressure Gauge on Basket Strainer DP Gauge |  | Wika | Not Labeled | 0.25 in. 0 - 100 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 2 Pressure Gauge |  | Ashcroft | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 1 Pressure Gauge 10 |  | Ashcroft | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue line 3 Pressure Gauge at DP |  | Not Labeled | Not Labeled | 0.25 in. 0 - 70 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue line 3 Pressure Gauge Pump Discharge |  | Not Labeled | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Receipt filter separator pressure gauge |  | Not Labeled | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Surge arrestor 2 gauge |  | Bar | Not Labeled | 0.25 in. 0 - 600 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue Pump 1 Vacuum Gauge |  | Ashcroft | Not Labeled | 0.25 in. -30 - 160 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Check Stand |  | Palmer | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Issue line 1 F/S DP Gauge |  | Wika | Not Labeled | 0.25 in. 0 - 30 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Hydrant Return Loop Pressure Gauge |  | Wika | Not Labeled | 0.5 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Hydrant Return Loop Pressure Gauge |  | Wika | Not Labeled | 1.0 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Receipt Separator DP Gauge |  | Not Labeled | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | Separator 2D DP Gauge |  | Not Listed | Not Listed | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure and Pressure/Vacuum Gauges | BPCV Line |  | Wika | Not Labeled | 0.25 in. 0 - 160 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Issue Pump 3 Basket Strainer dp gauge |  | Schultz | Sc-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Issue Pump 1 Differential Gauge on Basket Strainer |  | Schultz | SC -5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Separator 2E |  | Schultz | Sc-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Separator 2D |  | Schultz | SC-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Issue Pump 2 Differential Gauge on Basket Strainer |  | Not Labeled | Not Labeled | 0 - 300 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Separator 2C |  | Schultz | Sc-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Gauges | Receipt Separator |  | Schultz | SC-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Pressure Transmitters | Pressure Transmitter (PIT) |  | Siemens | 7MF4033-1EA10-1NC267-Z | GPM/SCFM 9.15 - 915 PSI | X | X | X | 6-7.3 | Regularly check the pressure transducer pressure connections for leaks, and tighten as needed. Also, keep all electrical connections between the system and components free of water and spray. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Transmitters | DPT |  | Siemens | 7MF4433-1EA22-1NC7-Z | N/A | X | X | X | 6-7.4 | Inspect the exterior of the transmitter enclosure for accumulated oil, dust, and dirt. Clean as required. Inspect the display viewing glass for cleanliness and damage. Replace the enclosure cap assembly if the glass is damaged or missing. No accumulation of dust, dirt, or water (condensate) should be present inside the enclosure. Check operation of transmitter. Ensure transmitter is indicating accurate pressure of the system. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Differential Pressure Transmitters | DPT |  | Siemens | 7MF4433-1FA22-1NC7-Z | N/A | X | X | X | 6-7.4 | Inspect the exterior of the transmitter enclosure for accumulated oil, dust, and dirt. Clean as required. Inspect the display viewing glass for cleanliness and damage. Replace the enclosure cap assembly if the glass is damaged or missing. No accumulation of dust, dirt, or water (condensate) should be present inside the enclosure. Check operation of transmitter. Ensure transmitter is indicating accurate pressure of the system. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | EFSO Systems | South Side of Canopy |  | Cooper Crouse Hinds | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Motor Controls | Issue Pump 3 |  | Not Labeled | Not Labeled | Not Labeled | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS |  | No data plate
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Motor Controls | Issue Pump 1 |  | Not Labeled | Not Labeled | Not Labeled | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Motor Controls | Issue Pump 2 |  | Not Labeled | Not Labeled | Not Labeled | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Motor Controls | Product Saver |  | Adalet | NCE181496 N4 | NCE181496 N5 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | North Column 2 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | North Column 3 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | North Column 4 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | North Column 5 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | South Column 1 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | South Column 2 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | South Column 3 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | South Column 4 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | South Column 5 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | South Side Fillstand Low Point Drain |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | North Side Fillstand Low Point Drain |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Issue line 3 separator ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Issue Pump 1 Separator 1 Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Product Saver |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Issue Pump 1 Pump/Motor Skid Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Issue Pump 2 Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Issue Pump 2 Separator Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Receipt filter separator ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | Hydrant Test Stand/Flush Station Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Static Grounding Systems | North Column 1 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Electric Motors | Issue Pump 3 motor |  | Baldor Reliance | Mel200149 | 100 HP | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Electric Motors | Issue Pump 1 Motor |  | Baldor Reliance | MEL2000149 | 100 HP | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Electric Motors | PRT Pump Motor |  | Baldor Reliance | B94658331 | 3450 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Electric Motors | Issue Pump 2 Motor |  | Baldor Reliance | MEL2000149 | 100 HP | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Lighting | Issue Pad |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Lightning Protection Systems | Issue Pad |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Coatings/Markings and Signage | Issue Pad |  | N/A | N/A | N/A | X | X | 0 | Coatings/Markings and Signage | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Containment Systems | Facility 981 Containment |  | N/A | N/A | N/A | 0 | 0 | X | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Canopies | Receipt Pad |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Emergency Eyewash/Showers | Receipt Pad |  | Not Labeled | Not Labeled | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Signage and Markings | Receipt Pad |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Automatic Air Vents | F/S 2A Air Eliminator |  | Armstrong | 11AV | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Automatic Air Vents | F/S 2B Air Eliminator |  | Armstrong | 11AV | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Automatic Air Vents | PRT Air Eliminator |  | Protectoseal | 6672 | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Filter Separators | F/S 2B |  | Facet | VCS-643-236 | 600 GPM GPM/SCFM 100 Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Filter Separators | F/S 2A |  | Facet | VCS-643-236 | 600 GPM GPM/SCFM 300 Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Centrifugal Pumps | PRT |  | Goulds | 1SV5NA3A30-M01 | 0-15 GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Filter Separator Control Valves | F/S 2B Discharge Side |  | Cla-Val | 150/PN16 | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Filter Separator Control Valves | F/S 2A |  | Cla-Val | 6/150MM | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Aboveground Piping | Receipt Lines |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Aboveground Piping | Receipt Line |  | N/A | N/A | 6.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Sight Flow Indicators | F/S 2B Sight Glass |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Sight Flow Indicators | F/S 2A Sight Glass |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Sight Flow Indicators | PRT Sight Glass |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Drain |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Discharge Sample Cock |  | Gammon Tech Products | 316 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A DP Gauge Discharge |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A DP Gauge Inlet |  | Not Labeled | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Air Eliminator Drain |  | Flo-Tite | T23SS | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Air Eliminator Discharge |  | Apollo | CF8M | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Discharge/PRV Isolation/Inlet |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Discharge Isolation |  | Flow-Tek | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Discharge Side Main Line Drain |  | Not Labeled | CF8M | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Discharge Valve O-26-NO |  | Flow-Tek | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Bypass PRV |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Pressure Relief Isolation Valve for A10 |  | Flow-Tek | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Pressure Relief Isolation Valve for A10 Receipt Line 3 |  | Flow-Tek | RF 15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Main Receipt Line Pressure Relief Isolation Valve Inlet to A14 |  | Flow-Tek | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Main Receipt Line Pressure Relief Isolation Valve for A14 |  | Flow-Tek | SF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Inlet Valve O-24-NO |  | Flow-Tek | FTG22 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Inlet Sample Cock |  | Gammon Tech Products | 316 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Drain Valve |  | Flow-Tek | SF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Drain Valve |  | Flow-Tek | SF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A PRV Test Port |  | Gammon Tech Products | GTP-992-4MS | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Inlet Pressure Relief Isolation Valve for A11 |  | Flow-Tek | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Outlet Pressure Relief Isolation Valve for A11 |  | Flow-Tek | RF15 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Discharge Valve O-25-NO |  | Flow-Tek | FTG22 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Slow Fill Isolation Valve |  | Flow-Tek | SF15 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Discharge Valve O-27-NO |  | Flow-Tek | RF15 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Pressure Relief Isolation Valve Receipt Line 3 |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Sample Port Isolation Valve |  | Not Labeled | Not Labeled | 0.66 (1/8th) in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Sample Port Isolation Valve |  | Gammon Tech Products | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Main Pressure Relief Line Valve |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Outlet Differential Pressure Gauge Isolation Valve |  | Not Labeled | Not Labeled | 0.66 (1/8th) in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Inlet Differential Pressure Gauge Isolation Valve |  | Not Labeled | Not Labeled | 0.66 (1/8th) in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Outlet Sample Port Valve |  | Not Labeled | Not Labeled | 0.66 (1/8th) in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | PRT Drain |  | Flo-Tite | SF150 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | PRT Discharge |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | PRT Return |  | Flow-Tek | WCB | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Main Receipt Line PRV Isolation |  | Flow-Tek | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Receipt Bypass Line O-20NC |  | Nibco | F510-CSR-66-FS | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Receipt Line Slow Fill |  | Flow-Tek | 316SS | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | PRV Line Isolation |  | Not Labeled | Not Labeled | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | PRV Line Drain (Beneath Receipt Line 2) |  | Not Labeled | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Pressure Relief Isolation Valve for A12 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A PRV Discharge |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Pressure Relief Isolation Valve for A12 |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Drain Valve Air Eliminator Line |  | Flo-Tite | CF8M | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A PRV Isolation Discharge |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Sump Drain Valve |  | Apollo | 88A20401 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A PRV Isolation Lower |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2B Sump Drain Valve |  | Apollo | 88A20401 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Drain (Capped Off) |  | Apollo | 88A20401 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Drain to Main Line |  | Apollo | 88A20401 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Drain to PRV Line |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Main Receipt Line Valve O-23-NC |  | Nibco | F510-CS-R-66FS | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | F/S 2A Inlet Isolation |  | Flow-Tek | FTG22 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Receipt Line 1 Drain |  | Flow-Tek | RF15-2 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Receipt Line 1 Drain Line |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Ball Valves | Recept Line 1 PRV Isolation |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Double Block and Bleed Valves | F/S 2B Valve O-22-NO Receipt Line 4 |  | Franklin Valve | D711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Double Block and Bleed Valves | F/S 2B Valve O-21-NO Receipt Line 3 |  | Franklin Valve | D711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Double Block and Bleed Valves | Receipt Line 2 Isolation O-16-NO |  | Franklin Valve | 4-150 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Double Block and Bleed Valves | Main Receipt Line Isolation O-19-NC |  | Duraseal | D711 | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Double Block and Bleed Valves | Receipt Line 1 |  | Franklin Valve | D711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Globe Valves | F/S 2B Sight Glass |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Globe Valves | F/S 2B Lower Sight Glass Valve |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Globe Valves | PRT Sight Glass Lower |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Globe Valves | PRT Sight Glass Upper |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Globe Valves | F/S 2A Sight Glass Lower |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Globe Valves | F/S 2A Sight Glass Upper |  | Kenco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Check Valves | PRT Fill Line |  | Titan | CV 44 | 2.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Check Valves | PRT Discharge |  | Not Labeled | CF8M | 1.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Check Valves | F/S 2B Air Eliminator Line Top of F/S |  | Apollo | CF8M | 0.75 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Check Valves | F/S 2A Air Eliminator Discharge |  | Apollo | CF8M | 0.75 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | F/ 2B Pressure Relief Valve A10 |  | Taylor | T-8200-1 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | Main Receipt Line Pressure Relief Valve A14 |  | Taylor | T-8200-1 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | F/S 2B |  | Taylor | T-8200-1 | 1.0 in. 227 - 450 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | A7 Receipt Line 1 |  | Taylor | T-8200-1 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | A9 F/S 2A PRV |  | Taylor | T-8200-1 | 1.0 in. 226 - 450 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | F/S 2A |  | Taylor | T-8220-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | F/S 2B Pressure Relief Valve A11 |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Thermal and/or Pressure Relief Valves | A13 Main Receipt Line |  | Taylor | T-8200-1 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Pressure and Pressure/Vacuum Gauges | F/S 2B Discharge Pressure Gauge |  | Trerice | Not Listed | 1.0 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Pressure and Pressure/Vacuum Gauges | F/S 2B Top of Differential Pressure Gauge |  | Bar | Not Listed | 0.25 in. 0 - 160 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Pressure and Pressure/Vacuum Gauges | F/S 2A DP Gauge |  | Not Labeled | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Differential Pressure Gauges | F/S 2A DP Gauge |  | Schultz | SC-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Differential Pressure Gauges | F/S 2B |  | Schultz | SC-5150-30 | 0 - 30 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Product Saver Tanks | PRT |  | Not Labeled | Not Labeled | 50 Gallons | X | X | 0 | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Externally Mounted Level Alarms | Receipt Pad (Main Tanks / PRT) |  | Not Labeled | Not Labeled | N/A | 0 | 0 | 0 | 8-9.9.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Motor Controls | PRT Controls |  | Siemens | 18DP92HDF81 | 18DP92HDF82 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | West Column 2 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | West Column 3 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | West Column 4 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | East Column 4 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | East Column 3 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | East Column 2 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | F/S 2A |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | PRT Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | PRT to Panel Board |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | East Column 1 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Static Grounding Systems | West Column 1 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Electric Motors | PRT |  | Baldor Reliance | B94658332 | 40C AMB-CONT | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 982 | Receipt Pad / Canopy | Receipt Pad | Lighting | Receipt Pad |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Lightning Protection Systems | Receipt Pad Canopy |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 982 | Receipt Pad / Canopy | Receipt Pad | Coatings/Markings and Signage | Receipt Pad |  | N/A | N/A | N/A | X | X | 0 | Coatings/Markings and Signage | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 983 | Maintenance Shed | Maintenance Shed | Pumphouse/Filter Buildings | Maintenance Shed |  | N/A | N/A | N/A | X | X | X | 11-2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 983 | Maintenance Shed | Maintenance Shed | EFSO Systems | Outside of Main Gate |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 986 | Refueler Parking Yard | Refueler Parking Yard | Fuel Truck Containment Areas | Parking Yard |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 986 | Refueler Parking Yard | Refueler Parking Yard | Canopies | Refueler Wash Rack |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 986 | Refueler Parking Yard | Refueler Parking Yard | Emergency Eyewash/Showers | Refueler Parking Yard |  | Bradley | N/A | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 986 | Refueler Parking Yard | Refueler Parking Yard | Oil/Water Separators | Refueler Parking Yard / RFM |  | Not Labeled | Not Labeled | N/A | X | X | X | 11-5 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 986 | Refueler Parking Yard | Refueler Parking Yard | Signage and Markings | Refueler Parking Yard |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 986 | Refueler Parking Yard | Refueler Parking Yard | Lighting | Refueler Parking Yard |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Canopies | Dispensers |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Signage and Markings | Dispenser / Canopy |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Pressure and Pressure/Vacuum Gauges | Pressure Gauge on Dispenser 3/4 Shear Valve |  | Wika | Not Labeled | 0.25 in. 0 - 100 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Pressure and Pressure/Vacuum Gauges | Dispenser 1/2 Shear Valve |  | ENFM | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Emergency Shutoff Valves | Dispenser 3/4 |  | OPW | Not Listed | 2.0 in. | 0 | 0 | X | 7-12 | Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. Inspect mechanical links of the valve for correct operation. Conduct test of valve to ensure it operates correctly. | Monthly - Inspect stabilizer bar to ensure that it is securely mounted below the base of the dispenser. Inspect the mounting bolts that secure the emergency shutoff valve to the stabilizer bar. Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Emergency Shutoff Valves | Dispenser 1/2 |  | OPW | Not Listed | 2.0 in. | 0 | 0 | X | 7-12 | Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. Inspect mechanical links of the valve for correct operation. Conduct test of valve to ensure it operates correctly. | Monthly - Inspect stabilizer bar to ensure that it is securely mounted below the base of the dispenser. Inspect the mounting bolts that secure the emergency shutoff valve to the stabilizer bar. Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Sumps | Dispenser 3/4 |  | Wayne | Not Labeled | N/A | X | X | X | 7-13 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Sumps | Dispenser 1/2 |  | Wayne | Not Labeled | N/A | X | X | X | 7-13 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Nozzles | Dispenser 4 |  | OPW | Not Labeled | 0.75 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Nozzles | Dispenser 3 |  | OPW | Not Labeled | 0.75 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Nozzles | Dispenser 1 |  | Catlow | Not Labeled | 1.0 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Nozzles | Dispenser 2 |  | Catlow | Not Labeled | 1.0 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Hoses | Dispenser 4 |  | Irpco | 339 | 0.75 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Hoses | Dispenser 3 |  | Steel Flex | 559N | 0.75 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Hoses | Dispenser 1 |  | Irpco | Not Labeled | 1.0 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Hoses | Dispenser 2 |  | Irpco | Steel Flex | 1.0 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Breakaways | Dispenser 4 |  | Catlow | CTM75 | 0.75 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Breakaways | Dispenser 3 |  | OPW | 66REC | 0.75 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Breakaways | Dispenser 1 |  | Catlow | CTM100 | 1.0 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Breakaways | Dispenser 2 |  | Catlow | CTM75 | 1.0 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Swivels | Dispenser 2 |  | Catlow | C720 | 1.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Swivels | Dispenser 1 |  | Catlow | C720 | 1.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Swivels | Dispenser 3 |  | OPW | 45 Series | 0.75 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Swivels | Dispenser 4 |  | Catlow | C720 | 0.75 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Hose Retriever | Dispenser 2 |  | Wayne | Dresser | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Hose Retriever | Dispenser 4 |  | Wayne | Dresser | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Hose Retriever | Dispenser 3 |  | Wayne | Dresser | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Hose Retriever | Dispenser 1 |  | Wayne | Dresser | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Cabinet | Dispenser 3/4 MOGAS |  | Wayne | 3/G7242D/2GHJ/HK | N/A | 0 | 0 | X | 7-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Cabinet | Dispenser 1/2 Diesel |  | Wayne | 3/G7242D/2GHJ/HK | N/A | 0 | 0 | X | 7-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Meters | Dispenser 3 |  | Wayne | DM2 | .3 - 19 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Meters | Dispenser 4 |  | Wayne | DM2 | .3 - 19 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Meters | Dispenser 2 |  | Wayne | DM 2 | .3 - 19 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Meters | Dispenser 1 |  | Wayne | DM 2 | .3 - 19 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Filters | Dispenser 4 |  | Cim-Tek | 400MB-30 | N/A | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Filters | Dispenser 3 |  | Cim-Tek | 400MB-30 | N/A | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Filters | Dispenser 2 |  | Cim-Tek | 400-30 | N/A | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Dispenser Filters | Dispenser 1 |  | Cim-Tek | 400-30 | N/A | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Static Grounding Systems | Dispenser Canopy West Column |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Lighting | Dispenser Canopy |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Card and Key Locks | FMU |  | FuelMaster | FMU 2500 | Not Labeled | 0 | 0 | X | 9-3 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 1145 | Canopy / Dispensers | Canopy / Dispensers | Lightning Protection Systems | Dispenser Canopy |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Canopies | Canopy 1146 |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Emergency Eyewash/Showers | Canopy 1146 eyewash/shower |  | Bradley | Not Listed | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact |  | Tag disintegrated
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Signage and Markings | Canopy 1146 signage |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Positive Displacement Meters | Canopy 1146 Mogas meter register |  | Liquid Controls | M-7-1 | 10-100 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Positive Displacement Meters | Diesel meter |  | Liquid Controls | M-7-1 | 10-100 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Fueling Nozzles | Diesel loading arm nozzle |  | Carter | C221810 | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Fueling Nozzles | Canopy 1146 Mogas loading arm nozzle |  | OPW | 1711DL-AL20 | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS |  | 2
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Aboveground Piping | Canopy 1146 Mogas piping |  | N/A | N/A | 2.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Aboveground Piping | Canopy 1146 Mogas piping |  | N/A | N/A | 3.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Aboveground Piping | Diesel piping |  | N/A | N/A | 2.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Aboveground Piping | Diesel piping |  | N/A | N/A | 3.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Gate Valves | Fillstand Containment Drain |  | PIV | Mueller | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Diesel Arm Kamlock 2 |  | Jomar | Not Legible | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Diesel Arm Kamlock 2 |  | Jomar | Not Legible | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Diesel Isolation |  | Not Legible | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Diesel gauge isolation |  | Jomar | 1000 WOG | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Diesel ball valve from meter |  | Jomar | Not Listed | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Canopy 1146 MOGAS Ball Valve at Concrete |  | Painted Over | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Canopy 1146 MOGAS Gauge Isolation |  | Painted Over | Painted Over | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Canopy 1146 MOGAS Gauge Isolation |  | Not Legible | Not Legible | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Canopy 1146 MOGAS Test Port |  | Not Legible | Not Legible | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Ball Valves | Canopy 1146 MOGAS Drain Line |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Pressure and Pressure/Vacuum Gauges | Canopy 1146 Mogas gauge |  | Wika | Not Labeled | 0.5 in. 0 - 100 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Pressure and Pressure/Vacuum Gauges | Diesel pressure gauge |  | Wika | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | EFSO Systems | Diesel Tank Side EFSO |  | Appleton | Cooper Crouse Hinds | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | EFSO Systems | Canopy 1146 EFSO Mogas |  | Cooper Crouse Hinds | Cl II, e, f, g, CL III | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Swivels | Diesel Swivel at Nozzle |  | OPW | 3075F0-0202-GL | 2.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Swivels | Canopy 1146 Fillstand arm swivel at elbow |  | OPW | DOVE CF-3 | 2.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Swivels | Diesel loading arm swivel at elbow |  | DOVE CF-3 | Not Labeled | 2.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Swivels | Canopy 1146 Mogas loading arm swivel- at nozzle |  | OPW | 3975FO-0202-GL | 2.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Containment Systems | Canopy 1146 containment |  | N/A | N/A | N/A | 0 | 0 | 0 | 8-10.1 | No Manufacturer Requirements Available | Daily - Inspect containment systems for cleanliness, if accessible. | No Mission Impact |  | Has issues draining. Drains to OWS in shop that over flows
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Motor Controls | Diesel side motor controls |  | Appleton | EFCDC2868 | EFCDC2869 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Motor Controls | Canopy 1146 Mogas motor controls |  | Appleton | EFDC2868 | EFDC2869 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Power Grounding Systems | Diesel Scully / Intellitrol |  | Scully | OGV | OGV | 0 | 0 | X | 9-1.6.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Power Grounding Systems | Canopy 1146 Mogas scully Intellitrol |  | Scully | OGV | OGV | 0 | 0 | X | 9-1.6.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Static Grounding Systems | Canopy 1146 ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1146 | Canopy / Fillstands | Canopy / Fillstands | Lighting | Canopy 1146 lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact |  | Non led
| 1148 | SSTA Tanks | SSTA Tanks | Emergency Eyewash/Showers | Tank Area |  | Not Labeled | Not Listed | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Signage and Markings | Tank Area |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Basket Strainers | Diesel Offload |  | Keckley | Style B | 3.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Basket Strainers | Receipt MOGAS Tank |  | Keckley | 250 | 3.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Centrifugal Pumps | Diesel Offload |  | ITT Marlow Pumps | 3PL3EL 433B608 | 150 GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Centrifugal Pumps | MOGAS Offload Pump |  | ITT Marlow Pumps | 3PL3EL | 150 GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Loading Fuel Hoses | Diesel tank hose |  | Hewitt | Not Labeled | 4.0 in. | X | X | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Loading Fuel Hoses | MOGAS tank |  | Not Labeled | Not Labeled | 4.0 in. | X | X | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Aboveground Piping | Diesel tank piping |  | N/A | N/A | 2.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Aboveground Piping | MOGAS tank piping |  | N/A | N/A | 3.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Aboveground Piping | MOGAS tank piping |  | N/A | N/A | 2.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Aboveground Piping | Diesel tank piping |  | N/A | N/A | 2.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Sight Flow Indicators | Diesel Offload |  | OPW | A216 | A216 | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Sight Flow Indicators | MOGAS Offload |  | OPW | A216 | A216 | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Gate Valves | Diesel Tank Pressure Relief |  | Not Accessible | Not Accessible / No Fall Protection | 0.5 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Gate Valves | MOGAS Tank Issue Pressure Line |  | Kunkle Valve Div. | 515 | 0.75 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Visi-Flow Drain |  | Painted Over | Painted Over | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Offload |  | Velan | Painted | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Sample Cock |  | Gammon Tech Products | GTP-1149 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Offload |  | Nibco | CF8M | 3.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Pump Discharge |  | Nibco | CF8M | 3.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Pump Discharge gauge Isolation |  | Nibco | Painted Over | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Line Drain |  | Painted/Corroded | Painted Over | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel tank ball valve |  | Not Legible | Not Legible | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Tank Top Vent Drain |  | Not Accessible / No Fall Protection | Unknown | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Diesel Tank |  | Painted Over | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Containment Drain Valve, Diesel Tank Side |  | Sharpe | CF8M | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | Containment Drain Valve, MOGAS Tank Side |  | Sharpe | CF8M | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Remote Dispenser Pump Isolation |  | Painted Over | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Pressure Relief Isolation |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Tank Line Drain |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Tank Return Line Isolation |  | Painted Over | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Discharge Line Isolation |  | Painted Over | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Offloading Sample Valve |  | Gammon Tech Products | GTP-1149 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Offload |  | Painted Over | Painted Over | 3.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Offload Drain Valve |  | Painted Over | Painted Over | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Ball Valves | MOGAS Offload Pump Drain Valve |  | Painted Over | Painted Over | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Check Valves | Diesel Tank Offload Check Valve |  | Nibco | 40058 | 3.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Check Valves | MOGAS Offload Check Valve |  | Nibco | 40058 | 3.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Pressure and Pressure/Vacuum Gauges | MOGAS Offload Pressure Gauge |  | Wika | Not Labeled | 0.25 in. 0 - 100 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Pressure and Pressure/Vacuum Gauges | Diesel Pump Discharge |  | Work Smart | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Transition Sumps | Diesel |  | Not Labeled | Not Labeled | N/A | X | X | X | 7-14 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Transition Sumps | MOGAS |  | Not Labeled | Not Labeled | N/A | X | X | X | 7-14 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Remote Dispenser Pumps | Diesel Dispenser Pump |  | Not Accessible / No Fall Protection | Not Accessible / No Fall Protection | 25 GPM/SCFM | X | X | 0 | 7-15.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Remote Dispenser Pumps | MOGAS tank pump |  | Not Accessible / No Fall Protection | Not Accessible / No Fall Protection | 25 GPM/SCFM | X | X | 0 | 7-15.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | No ladder
| 1148 | SSTA Tanks | SSTA Tanks | EFSO Systems | Diesel Side |  | Painted Over | Painted Over | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | EFSO Systems | MOGAS Side |  | Not Marked | Not Marked | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Dispenser Filters | Diesel Tank Top 1 |  | Petro Clear | 51130W | N/A | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Dispenser Filters | Diesel Tank Top 2 |  | Petro Clear | 51130W | N/A | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Aboveground Shop Fabricated Tanks | Diesel Tank |  | Modern Welding Company | MWCFG-9611 | 10,000 Gallons | X | X | X | 8-5.1 | No Manufacturer Requirements Available | Monthly - Visually inspect for evidence of leaks; shell distortions; signs of settlement; corrosion, condition of tank foundation, condition of coating, insulation systems, and appurtenances. Inspection shall include all components and equipment located inside the containment area such as piping, pipe supports, containment valves, and product saver tanks. Items noted during the inspection will be documented for follow-up action by an authorized inspector. See Appendix F for the Field-Erected Tank Monthly Inspection Checklist. Visually inspect chime to ringwall sealant. Seal should be maintained in good working order to prevent corrosion of the underside of the tank bottom. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Aboveground Shop Fabricated Tanks | MOGAS Tank |  | Modern Welding Company | MWCFG-9611 | 10,000 Gallons | X | X | X | 8-5.1 | No Manufacturer Requirements Available | Monthly - Visually inspect for evidence of leaks; shell distortions; signs of settlement; corrosion, condition of tank foundation, condition of coating, insulation systems, and appurtenances. Inspection shall include all components and equipment located inside the containment area such as piping, pipe supports, containment valves, and product saver tanks. Items noted during the inspection will be documented for follow-up action by an authorized inspector. See Appendix F for the Field-Erected Tank Monthly Inspection Checklist. Visually inspect chime to ringwall sealant. Seal should be maintained in good working order to prevent corrosion of the underside of the tank bottom. | Partial System OOS |  | Weight 25,000 pounds
| 1148 | SSTA Tanks | SSTA Tanks | Fill Ports | Receipt MOGAS Tank |  | Not Legible | Not Legible | 3.0 In. | X | X | X | 8-9.12 | Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. | Daily - Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. Ensure the spill bucket is clean of dirt, trash, water, and fuel. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Fill Ports | Diesel Tank Offload |  | Not Legible | Not Legible | 3.0 In. | X | X | X | 8-9.12 | Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. | Daily - Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. Ensure the spill bucket is clean of dirt, trash, water, and fuel. | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Tank Pressure/ Vacuum Vents | Diesel Tank Vent |  | OPW | 523V-1100 | N/A | 0 | 0 | X | 8-9.3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Tank Pressure/ Vacuum Vents | Mogas tank vent |  | OPW | 523V-1100 | N/A | 0 | 0 | X | 8-9.3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Emergency Vents | Diesel 1 |  | Morrison Brothers | Not Accessible / No Fall Protection | 6.0 In. | 0 | 0 | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Emergency Vents | Diesel Tank #2 Vent |  | Morrison Brothers | Not Accessible / No Fall Protection | 6.0 In. | 0 | 0 | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Emergency Vents | MOGAS Tank Emergency Vent 1 |  | Morrison Brothers | Not Accessible / No Fall Protection | 6.0 In. | 0 | 0 | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Emergency Vents | MOGAS Tank Emergency Vent 2 |  | Morrison Brothers | Not Accessible / No Fall Protection | 6.0 In. | 0 | 0 | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Servo Gauge | MOGAS tank clock gauge |  | Morrison Brothers | Not Accessible / No Fall Protection | N/A | X | X | X | 8-9.8.3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Servo Gauge | Diesel Clock Gauge |  | Morrison Brothers | Not Accessible / No Fall Protection | N/A | X | X | X | 8-9.8.3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Motor Controls | MOGAS |  | Not Labeled | EFKB-U2 | EFKB-U3 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Motor Controls | Diesel Pump |  | Not Labeled | EFKBJ2 9/95 | EFKBJ2 9/96 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Mogas Tank Ground Rear Right- by skid |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | MOGAS tank rear left ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | MOGAS Tank Front Right Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | MOGAS Tank Front Left Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Diesel tank ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Diesel tank ground front right |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Diesel tank rear left ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Diesel rear right ground- by pump |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Diesel pump skid ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Static Grounding Systems | Mogas pump skid ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Electric Motors | Diesel Pump |  | Baldor Reliance | AJ622091 | 1860 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 1148 | SSTA Tanks | SSTA Tanks | Electric Motors | MOGAS Offload Motor |  | Baldor Reliance | AJ622094 | 40CAMB-CONT 75C RISE | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS |  | Grease: EXXONPLOYREX EM
| 1148 | SSTA Tanks | SSTA Tanks | Lighting | Tank Area |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Coatings/Markings and Signage | MOGAS Tank |  | N/A | N/A | N/A | X | X | 0 | Coatings/Markings and Signage | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Coatings/Markings and Signage | Diesel Tank |  | N/A | N/A | N/A | X | X | 0 | Coatings/Markings and Signage | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1148 | SSTA Tanks | SSTA Tanks | Containment Systems | Diesel / MOGAS Tanks |  | N/A | N/A | N/A | 0 | 0 | X | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1154 | SSTA Ops Building | SSTA Ops Building | Pumphouse/Filter Buildings | Bldg 1154 Ops |  | N/A | N/A | N/A | X | X | X | 11-2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | ATG inside
| 1154 | SSTA Ops Building | SSTA Ops Building | Signage and Markings | Bldg 1154 signage |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Access door missing no smoking sign
| 1154 | SSTA Ops Building | SSTA Ops Building | EFSO Systems | Bldg 1154 EFSO |  | Appleton | N2D75FA-U1 | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 1154 | SSTA Ops Building | SSTA Ops Building | Static Grounding Systems | Bldg 1154 grounding |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 1176 | Smoke Pit | Smoke Pit | Pumphouse/Filter Buildings | Bldg 1176 Smoke Pit |  | N/A | N/A | N/A | X | X | X | 11-2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1178 | Fuels Management Building | Fuels Management Building | Pumphouse/Filter Buildings | Bldg 1178 fuel Ops |  | N/A | N/A | N/A | X | X | X | 11-2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 1178 | Fuels Management Building | Fuels Management Building | Emergency Eyewash/Showers | Laboratory Eyewash |  | Water Saver Faucet | Not Listed | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 1178 | Fuels Management Building | Fuels Management Building | Ventilation Hoods | Fume Hood |  | Fisher Hamilton | Safeaire | N/A | X | X | X | 11-4.1 | Daily visual inspection, check the fume hood for visible airflow blockage such as large items or containers near the slot opening. Other daily inspections include holding a tissue at the opening to observe inward airflow, maintaining clean surfaces inside the hood, and keeping the sash at an appropriate height when working and not working in the hood. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 1 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Capped Off
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 1 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 2 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Capped Off
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 2 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 4 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 3 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 3 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 5 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 5 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 6 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 6 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Automatic Air Vents | Isolation Pit 4 |  | Armstrong | 11S | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 1 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 1 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 5 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 8 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 10 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 3 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 2 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 6 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 7 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 9 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 11 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 12 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Control Valves | Pit 13 |  | Cla-Val | 362AF-8-SKX | 4.0 in. | X | X | 0 | 4-4.2.8 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 3 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 4 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 5 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 2 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 6 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 8 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 7 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 9 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 10 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 12 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 11 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 13 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Adapters | Pit 1 |  | Cla-Val | 364AF | 4.0 In. | X | X | 0 | 4-7.3 | Inspect hydrant adapter for proper operation, damage, and wear. Test operation of dry break system. | No Operator Requirement | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit West Side of Flightline |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit 2 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit 3 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit 4 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit 1 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Expansion Point East Side of Flightline |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit 5 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Isolation Valve Pits | Isolation Pit 6 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 1 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 2 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 3 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 5 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 4 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 6 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 7 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 8 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 9 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 10 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 11 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 12 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Hydrant Fuel Pits | Pit 13 |  | Dabico | DAB-725 | N/A | 0 | 0 | 0 | 6-11.2 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions - Hydrant fuel pits shall be inspected to ensure that they are dry and clean and that all fueling components within the pit are clean and in good working order. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Check for fuel leaks at all flanged and pipe connections.Check pit lids to ensure that seals are in good working order and are preventing water entry into the pits. Inspect hydrant fuel pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | High Point Vent Pits | High Point South West Corner |  | Dabico | Not Labled | 2.0 In. | 0 | 0 | 0 | 6-11.3 | No Manufacturer Requirements Available | Monthly - Inspect high point vent pits to ensure they are dry and free of water and other debris and that pit and piping components are leak free and in good working condition. Inspect the pit for fuel or water. Fuel or water found in the pit shall be sumped out as soon as possible. Check pipe penetrations through pit walls or bottom to ensure that mechanical and boot seals are in good working condition and are allowing no water seepage into the pits. Ensure that high point vent valves, quick-disconnect couplings or pit lids are lockable and that locking mechanisms are in good working order. Inspect high point vent pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Low Point Drain Pits | Low Point south East Corner of Flight Line |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.4 | No Manufacturer Requirements Available | Monthly - Inspect low point drain pits to ensure they are dry and free of water and other debris and that all pit and piping components are leak free and in good working condition. Inspect the pit for fuel or water. Fuel or water found in the pit shall be sumped out as soon as possible. Check pipe penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no water seepage into the pits. Check pit lid seals for deterioration and replace as necessary. Ensure that low point vent valves, quick-disconnect couplings or pit lids are lockable and that locking mechanisms are in good working order. Inspect low point drain pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Low Point Drain Pits | Low Point Pit 9 |  | Dabico | Cavotec | N/A | 0 | 0 | 0 | 6-11.4 | No Manufacturer Requirements Available | Monthly - Inspect low point drain pits to ensure they are dry and free of water and other debris and that all pit and piping components are leak free and in good working condition. Inspect the pit for fuel or water. Fuel or water found in the pit shall be sumped out as soon as possible. Check pipe penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no water seepage into the pits. Check pit lid seals for deterioration and replace as necessary. Ensure that low point vent valves, quick-disconnect couplings or pit lids are lockable and that locking mechanisms are in good working order. Inspect low point drain pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Surge Suppressor Pit |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 29.383474 -98.589318 Confined Space Required
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Low Point South East Corner of Lightline |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 3 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 4 |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Surge Suppressor Pit Center Flightline |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Comfined Space / Under Water
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 2 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 6 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 1, Gauge Isolation |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 4 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Confined Space
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 4, Air Eliminator Isolation |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Confined Space
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 8 |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 8, Gauge Isolation |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 5 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 12 |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 12 |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 13 |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 6 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Expansion Isolation East Side of Flightline |  | VGC | CF8M | 8.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 1 |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Surge Suppressor Pit /Disabled |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 29.381443 -98.592748
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Low Point Air Vent South East Corner of Flight Line |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 1, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 2, Isolation |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 3 |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 2, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 3 |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 4, Air Eliminator Isolation |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Confined Space
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 5 |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Surge Suppressor Pit East Side of Flghtline Row |  | Velan | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Confined Space Air Vent Valve
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | High Point Pit |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 29.382585 -98.592881
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 3 |  | Flow-Tek | CF8M | 12.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Lat 29.379096 Long -98.588767
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 6, Air Eliminator |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 13, Pressure Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 11 Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 10, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 7, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 7 |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 6, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 6 |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 4 |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 4 |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 5, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 5, Isolation |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 9, Isolation |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 9, Gauge Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 5 |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 10 |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Low Point Drain Pit |  | Velan | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 11, Isolation |  | Flo-Tite | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Hydrant Pit 12 |  | Watts | 8714 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 2, Air Eliminator |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Unknown
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 2, Air Eliminator |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Confined Space Entry Required
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Ball Valves | Isolation Pit 1, Air Eliminator |  | Velan | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 1 |  | Weston | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 2 |  | Weston | Not Labeled | 0.5 in. 0 - 30 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 3 |  | Weston | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 5 |  | Weston | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 4 |  | Weston | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 6 |  | Weston | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 7 |  | Weston | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 8 |  | Weston | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 9 |  | Weston | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 10 |  | Weston | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 11 |  | Weston | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 12 |  | Weston | Not Labeled | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | Pressure and Pressure/Vacuum Gauges | Pit 13 |  | Weston | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #1 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.383577 -98.588680
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #2 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.383278 -98.589720
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #3 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.383125 -98.590438
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #4 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.382883. -98.591460
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #5 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.382617 -98.592335
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #6 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.381879 -98.992593
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #7 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.381107 -98.592286
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #8 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.380794. -98.591135
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #9 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.381110 -98.589950
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #10 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.380968 -98.589378
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #11 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.379825 -98.589078
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #12 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.378712 -98.588672
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #13 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.377881 -98.588327
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #14 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.376784 -98.587866
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #15 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.376616 -98.587811
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #16 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.376016 -98.587020
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #17 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.376279 -98.586097
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #18 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.377127 -98.585667
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #19 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.377950 -98.585924
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #20 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.377950 -98.585924
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #21 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.379484 -98.586479
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #22 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.380481 -98.586822
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #23 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.381337 -98.587182
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #24 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.382096 -98.587440
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #25 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.382693 -98.587670
| 11100 | Hydrant Loop / Flightline | Hydrant Loop / Flightline | EFSO Systems | #26 |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 29.382693 -98.587670
| 11101 | Tank 1 | 11101 / Tank 1 | Signage and Markings | Tank 11101 |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Automatic Air Vents | Tank 11101 |  | N/A | N/A | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Centrifugal Pumps | Product Saver |  | Corcoran Pumps | 20000 | 0-15 GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Pressure Control Valves | Tank 11101 Return Line |  | Cla-Val | 150 | 8.0 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Aboveground Piping | Tank 11101 Issue Line |  | N/A | N/A | 12.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Aboveground Piping | Tank 11101 Stripper Line |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Aboveground Piping | Tank 11101 Return Line |  | N/A | N/A | 6.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Gate Valves | Tank 11101 Dike Drain |  | Confined Space / Not Accessible | Unknown | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Return Line PRV Test Port M-98-NO |  | Gammon Tech Products | GTP-992-4MS | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Issue Line Low Point Drain Valve |  | Flow-Tek | SF15-2 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Issue Line Pressure Relief Test Port Valve |  | Gammon Tech Products | GTP-992-4MS | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Issue Line Pressure Relief Isolation Valve M-102-NO |  | Painted Over | CF8M | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Pump Inlet O-PR4-NC |  | Flow-Tek | CF8M | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Issue Line Pressure Relief Isolation Valve M-103-NO |  | Apollo | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Drain O-PR6-NC |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Sensing Line |  | Flow-Tek | F15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Return O-PR5-NC |  | Flow-Tek | 15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Fill |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Isolation O-PR2-NC |  | Merit | 316 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Product Saver Isolation O-PRI-NC |  | Not Labeled | Not Labeled | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Stripper Line Isolation O-92-NC |  | Nibco | 150 WCB | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Return Line Control Valve |  | Haitima | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Return Line Control Valve |  | Haitima | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Tank 11101 Return Line PRV Isolation |  | Haitima | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Tank 11101 Pressure Relief Line 1 |  | Nibco | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Ball Valves | Tank 11101 Auto Shut Off Line |  | Not Labeled | Not Labeled | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Double Block and Bleed Valves | Issue Line Double Block and Bleed Valve O-99-NC |  | Tru-Seal | 211 | 12.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | At the skin of the tank
| 11101 | Tank 1 | 11101 / Tank 1 | Double Block and Bleed Valves | Stripper Line Isolation |  | Not Legible | Not Legible | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Double Block and Bleed Valves | Tank 11101 Return Line |  | General Twin Seal | 8-150 | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Globe Valves | Product Saver |  | Not Labeled | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Globe Valves | Product Saver Upper |  | Not Labeled | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Check Valves | Product Saver Return |  | Velan | B | 1.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Thermal and/or Pressure Relief Valves | Issue Line Pressure Relief Valve A42 |  | Taylor | T-8250-1 | 0.75 in. 51 - 125 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Thermal and/or Pressure Relief Valves | A41 Return Line |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Flexible Ball Joints | Return Line |  | Advance Thermal Systems INC | S2 | 8.0 In. | X | X | 0 | 6-8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Flexible Ball Joints | Issue Line Flexible Ball Joint |  | Advance Thermal Systems INC | S2 | 6.0 In. | X | X | 0 | 6-8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Size 16
| 11101 | Tank 1 | 11101 / Tank 1 | Flexible Ball Joints | Issue Line Flexible Ball Joint |  | Advance Thermal Systems INC | S2 | 6.0 In. | X | X | 0 | 6-8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Size 16
| 11101 | Tank 1 | 11101 / Tank 1 | Dial Thermometer | Tank 1 Thermometer |  | Tel-Tru | Not Labeled | GPM/SCFM | X | X | X | 6-9.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Containment Systems | Tank 11101 |  | N/A | N/A | N/A | 0 | 0 | 0 | 8-10.1 | No Manufacturer Requirements Available | Daily - Inspect containment systems for cleanliness, if accessible. | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Aboveground Field-Erected Tanks | Tank 11101 |  | Henders Boiler and Tank Co. | G&H | 25,000 Barrels | 0 | 0 | X | 8-4 | No Manufacturer Requirements Available | Monthly - Visually inspect for evidence of leaks; shell distortions; signs of settlement; corrosion, condition of tank foundation, condition of coating, insulation systems, and appurtenances. Inspection shall include all components and equipment located inside the containment area such as piping, pipe supports, containment valves, and product saver tanks. Items noted during the inspection will be documented for follow-up action by an authorized inspector. See Appendix F for the Field-Erected Tank Monthly Inspection Checklist. Visually inspect chime to ringwall sealant. Seal should be maintained in good working order to prevent corrosion of the underside of the tank bottom. | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Product Saver Tanks | Product Saver |  | Not Labeled | Not Labeled | 50 Gals Gallons | X | X | 0 | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Mechanical Tape Gauges | Tank 11101 |  | GRE Controls | 92020 | N/A | X | X | 0 | 8-9.7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11101 | Tank 1 | 11101 / Tank 1 | Motor Controls | Product Saver |  | Appleton | EDSF12A | EDSF12A | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Static Grounding Systems | Product Saver |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | Static Grounding Systems | Tank 11101 Ground 1 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11101 | Tank 1 | 11101 / Tank 1 | External High Level Shutoff Valves | Tank 11101 |  | Cla-Val | Liquid Level | N/A | X | X | X | HLSO | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11102 | Tank 2 | 11102 / Tank 2 | Automatic Air Vents | Tank 11102 |  | N/A | N/A | N/A | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Centrifugal Pumps | Product Recovery Tank |  | Corcoran Pumps | 20000 | 0-15 GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Pressure Control Valves | Issue Line Pressure Control Valve for Double Block and Bleed Valve O-105-NC |  | Cla-Val | 81066018 | 1.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Pressure Control Valves | Return Line |  | Cla-Val | Mil-V-Flow | 8.0 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Aboveground Piping | Tank 2 Issue Line |  | N/A | N/A | 12.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Aboveground Piping | Stripper Line |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Aboveground Piping | Return Line |  | N/A | N/A | 8.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Gate Valves | Dike Drain VG-050 |  | Not Accessible | Not Accessible | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Issue Line Low Point Drain Valve |  | Flow-Tek | SF15-2 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Product Recovery Tank Drain Valve O-PR3-NC |  | Flow-Tek | CF8M | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Product Recovery Tank Drain Valve O-PR5-NC |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Product Saver Drain |  | Apollo | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Product Saver Issue O-PR4-NC |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Product Saver Fill Line O-PR2-NC |  | Flow-Tek | F15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Sensing Lines by Product Saver |  | Swagelok | Not Labeled | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Sensing Line by Product Saver |  | Swagelok | Not Labeled | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Return Line PRV Isolation |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Return Line PRV Isolation |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Tale Tale 4 |  | Smith-Cooper | 4798 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Tale Tale 3 |  | Smith-Cooper | 4798 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Tale Tale 2 |  | Smith-Cooper | 4798 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Ball Valves | Tale Tale 1 |  | Smith-Cooper | 4798 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Double Block and Bleed Valves | Stripper Line Tank Isolation |  | Tru-Seal | 4-150 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Double Block and Bleed Valves | Product Saver Main Tank Isolation O-PRI-NC |  | Tru-Seal | 2-150 | 2.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Double Block and Bleed Valves | Return Line Tank Isolation |  | General Twin Seal | 1-8108-04RG | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Double Block and Bleed Valves | Issue Line Double Block and Bleed Valve O-105-NC |  | General Twin Seal | 8811RF | 12.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Globe Valves | Product Saver Sight Glass Lower |  | Not Labeled | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Globe Valves | Product Saver Sight Glass Upper |  | Not Labeled | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Check Valves | Product Recovery Tank Check Valve |  | Velan | B | 1.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Thermal and/or Pressure Relief Valves | Return Line |  | Taylor | A40 T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Motor Operators | Issue Line Double Block and Bleed Operator Valve |  | WestLock Controls | Not Labeled | Not Labeled | X | X | 0 | 6-6.6 | Visually inspect motor operators to ensure smooth movement during opening and closing operation and adjust, if necessary, to ensure that they are opening and closing fully. Listen for and investigate unusual noises during operation. | No Operator Requirement | Partial System OOS |  | For Valve O-105-NC
| 11102 | Tank 2 | Tank 11102 | Flexible Ball Joints | Return Line |  | Advance Thermal Systems INC | S2 | 8.0 In. | X | X | 0 | 6-8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Flexible Ball Joints | Issue Line Flexible Ball Joints |  | Advance Thermal Systems INC | S2 | 6.0 In. | X | X | 0 | 6-8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 16
| 11102 | Tank 2 | Tank 11102 | Flexible Ball Joints | Issue Line Flexible Ball Joint |  | Advance Thermal Systems INC | S2 | 6.0 In. | X | X | 0 | 6-8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 16
| 11102 | Tank 2 | 11102 / Tank 2 | Aboveground Field-Erected Tanks | Tank 11102 |  | Henders Boiler and Tank Co. | G&H | 25,000 Barrels | 0 | 0 | X | 8-4 | No Manufacturer Requirements Available | Monthly - Visually inspect for evidence of leaks; shell distortions; signs of settlement; corrosion, condition of tank foundation, condition of coating, insulation systems, and appurtenances. Inspection shall include all components and equipment located inside the containment area such as piping, pipe supports, containment valves, and product saver tanks. Items noted during the inspection will be documented for follow-up action by an authorized inspector. See Appendix F for the Field-Erected Tank Monthly Inspection Checklist. Visually inspect chime to ringwall sealant. Seal should be maintained in good working order to prevent corrosion of the underside of the tank bottom. | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Product Saver Tanks | Product Recovery Tank |  | Gammon Tech Products | Unmarked | 55 Gallons | X | X | 0 | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Mechanical Tape Gauges | Tank 11102 |  | Varec | 2500 | N/A | X | X | 0 | 8-9.7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | Motor Controls | Product Recovery Tank |  | Appleton | EDSF12A | EDSF12A | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Static Grounding Systems | Tank 11102 2 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Static Grounding Systems | Product Saver |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Static Grounding Systems | Tank 11102 4 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Static Grounding Systems | Tank 11102 3 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Static Grounding Systems | Tank 11102 1 |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11102 | Tank 2 | Tank 11102 | Containment Systems | Tank 2 Containment |  | N/A | N/A | N/A | 0 | 0 | X | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11102 | Tank 2 | Tank 11102 | External High Level Shutoff Valves | Tank 11102 |  | Cla-Val | Liquid Level | N/A | X | X | X | HLSO | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Fuel Truck Containment Areas | North Side Containment |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Fuel Truck Containment Areas | South Side Containment |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Canopies | Offload Pad Canopy |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Emergency Eyewash/Showers | West Side Offload |  | Haws | 8317 | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Signage and Markings | Offload Area |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Automatic Air Vents | West Side Offload |  | Shand & Jurs | 94020-120142001 | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Automatic Air Vents | East Side Receipt Offload Vent on Static Tank |  | Shand & Jurs | 94020-120142001 | 1.0 In. | 0 | 0 | X | 3-10.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Basket Strainers | East Side Receipt Offload Basket Strainer |  | Titan | H562 | 6.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Basket Strainers | West Side Basket Strainer on Skid |  | Titan | BS85 | 2.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Basket Strainers | West Side Offload |  | Titan | BS85 | 6.0 in. | X | X | 0 | 3-6.4 | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Positive Displacement Meters | West Side Offload |  | Total Control Systems | 700-40SP3AG | 500 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Positive Displacement Meters | East Side Receipt Offload Meter |  | Total Control Systems | 700-40SP3AG | 40-500 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Centrifugal Pumps | East Side Receipt Offload Pump |  | ClydeUnion Pumps | CM110227A-1 | 300 gpm GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Centrifugal Pumps | West Side Offload |  | ClydeUnion Pumps | 3 X 4 X 10A VLK-L | 300 gpm GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Centrifugal Pumps | West Side Skid Pump |  | Gorman Rupp | 02K3-X2 1P | GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Offloading Fuel Hoses | Bowser Offload |  | Dixon | CS200-8ES | 2.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for cracks brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Offloading Fuel Hoses | West Side Offload Hose 1 |  | Kanaflex | Not Labeled | 4.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for cracks brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Offloading Fuel Hoses | West Side Offload Hose 2 |  | Kanaflex | Not Labeled | 4.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for cracks brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Offloading Fuel Hoses | East Side Receipt Offload Hose |  | Kanaflex | Not Labeled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for cracks brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Offloading Fuel Hoses | East Side Receipt Offload Hose - North |  | Kanaflex | Not Labeled | 4.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for cracks brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Non-Surge Check Valves | East Side Receipt Offload Control Valve |  | Cla-Val | 4/100MM | 4.0 in. | X | X | 0 | 4-4.2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Non-Surge Check Valves | West Side Offload |  | Cla-Val | 4/100MM | 4.0 in. | X | X | 0 | 4-4.2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Aboveground Piping | Offload Area |  | N/A | N/A | 3.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | West Side Offload 1 |  | Not Labeled | Not Labeled | Not Labeled | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | West Side Offload Offload 2 |  | Not Labeled | Not Labeled | Not Labeled | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | East Side Receipt Offload Static Chamber |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | West Side Offload static Chamber Upper |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | East Side Receipt Offload Lower Sight Glass |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | West Side Offload Static Chamber |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | East Side Receipt Offload Sight Flow Indicator |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | East Side Receipt Offload Sight Flow Indicator |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Sight Flow Indicators | West Side Visi-Flo on Skid |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Gate Valves | Confined Space Drain Valve |  | Not Accessible | Not Accessible | 10.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Basket Strainer Sample Cock |  | Gammon Tech Products | GTP-1149 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Valve O-7-NC |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Valve O-6-NC |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Sample Port Isolation Valve |  | Gammon Tech Products | Not Listed | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Outlet Pressure Relief Isolation Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Static Chamber Pressure Relief Isolation Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | Emergency Shower Isolation |  | Milwaukee Valve Company | 600 WOG | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Valve O-4-NO |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Inlet Pressure Relief Isolation Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Outlet Pressure Relief Isolation Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side RTB Inlet Pressure Relief Isolation Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Sample Port Isolation Valve |  | Gammon Tech Products | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Pressure Gauge Isolation Valve |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Pressure Gauge Isolation Valve |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Pressure Relief Isolation Valve |  | Flo-Tite | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Sample Port Isolation Valve |  | Gammon Tech Products | Not Labeled | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Drain Valve on Static Chamber |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Valve O-3-NO |  | Flow-Tek | CF8M | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Valve O-2-NC |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | East Side Receipt Offload Valve O1-NC |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | Bowser Skid |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Skid Pressure Relief Isolation Valve |  | Flow-Tek | Series RF15 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload PRV Test Port |  | Gammon Tech Products | CF8M | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Main Line Sample Cock |  | Gammon Tech Products | Not Legible | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload PRV Test Port |  | Gammon Tech Products | TP-9924MS | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Static Chamber PRV Test Port |  | Gammon Tech Products | GTP-19 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Discharge Valve O-BP1-NC on Skid |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Skid Discharge Valve O-BP1-NC |  | Flow-Tek | RF15 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Pressure Gauge Isolation Valve on Skid |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Skid Isolation Valve |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Skid Discharge Valve O-BP2-NC |  | Flow-Tek | RF15 | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Meter Drain |  | Haitima | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Basket Strainer Drain |  | Flow-Tek | F150 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Air Eliminator Drain |  | Flow-Tek | S40 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload O-8-NC |  | Flow-Tek | F15-4 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Hose Isolation O-9-NC |  | Flow-Tek | 4-150 | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload PRV Drain Isolation |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload O-10-NO |  | Flow-Tek | FTG22 | 6.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Static Chamber Drain |  | Flow-Tek | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Static Chamber PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Stat Chamber PRV Isolation |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Gauge Isolation Suction |  | Flow-Tek | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Gauge Isolation |  | Flow-Tek | F15 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload SPR Isolation |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload PRV Isolation Discharge |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload PRV Isolation Lower |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload Main Line Isolation O-11-NO |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload SPR Isolation U-14-NC |  | Flow-Tek | CF8M | 4.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Offload PRV Isolation Discharge |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Side Offload PRV Isolation Lower |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Ball Valves | West Offload Sample Cock |  | Accu-Sample | #6.360.619 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Double Block and Bleed Valves | West Offload Skid Isolation O-12-NC |  | Franklin Valve | 711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Double Block and Bleed Valves | East Side Receipt Offload Valve 0-5-NC |  | Franklin Valve | 4-150 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | West Side Offload static Chamber |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | West Side Offload Static Chamber |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | West Side Offload Static Chamber |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | East Side Receipt Offload Upper Globe Valve on Sight Glass |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | East Side Receipt Offload Lower Globe Valve on Sight Glass |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | East Side Receipt Offload Upper Globe Valve on Lower Sight Glass |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | East Side Receipt Offload Lower Globe Valve on Lower Sight Glass |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Globe Valves | West Side Offload Static Chamber |  | Ernst | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Check Valves | East Side Receipt Offload - South |  | Titan FCI | CV42/CV44 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Check Valves | East Side Receipt Offload - North |  | Titan FCI | CV42/CV44 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Check Valves | West Side Receipt Offload-North |  | Titan FCI | CV42/CV44 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Check Valves | West Side Receipt Offload- South |  | Titan FCI | CV42/CV44 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | East Side RTB Pressure Relief Valve A1 |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | West Side Offload Static Chamber |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | East Side Receipt Offload Pressure Relief Valve A3 |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | West Side Skid Pressure Relief Valve A43 |  | Taylor | T-7700-1 | 1.0 in. 30 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | A6 West Side Offload |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | A5 West Side Offload |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Thermal and/or Pressure Relief Valves | East Side RTB Pressure Relief Valve A2 |  | Taylor | T-8200-1 | 1.0 in. 101 - 225 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Pressure and Pressure/Vacuum Gauges | East Side Receipt Line Pressure Gauge |  | Not Labeled | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Pressure and Pressure/Vacuum Gauges | East Side Receipt Offload Pressure Gauge |  | Not Labeled | Not Labeled | 0.5 in. -30 - 60 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Pressure and Pressure/Vacuum Gauges | West Side Pressure Gauge on Skid |  | Palmer | Not Labeled | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Pressure and Pressure/Vacuum Gauges | West Side Skid Pressure Gauge |  | Palmer | Not Labeled | 0.5 in. 0 - 60 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Pressure and Pressure/Vacuum Gauges | West Side Offload Suction Side |  | Wika | Swiss Movement | 0.5 in. -30 - 60 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Pressure and Pressure/Vacuum Gauges | West Side Offload |  | Wika | Swiss Movement | 0.5 in. 0 - 160 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Differential Pressure Gauges | West Side Offload Basket Strainer |  | Gammon Tech Products | GTP-534-15 | 0 - 15 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Differential Pressure Gauges | East Side Receipt Offload Differential Pressure Gauge |  | Gammon Tech Products | GTP-534-15 | 0 - 16 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | EFSO Systems | East Side Offload EFSO |  | Akron Electric Inc | OX333-X-N4-N5 | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | EFSO Systems | South Side of Offload Racks (Grass) |  | Cooper Crouse Hinds | DS441 | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | EFSO Systems | West Side Offload Skid |  | Akron Electric Inc | CXI333X1N4N5 | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | EFSO Systems | West Side of Building |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Motor Controls | East Side Receipt Offload Control Panel |  | Akron Electric Inc | Not Labeled | Not Labeled | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Motor Controls | West Side Skid Motor Control |  | Akron Electric Inc | CAT. CX1363-MOD-08 | CAT. CX1363-MOD-09 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Motor Controls | West Side Offload |  | Akron Electric Inc | CXK18248H2N1N4N5C1N6 | CXK18248H2N1N4N5C1N7 | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Power Grounding Systems | West Side Offload Scully Ground |  | Scully | ST-47-ELK | ST-47-ELK | 0 | 0 | X | 9-1.6.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Power Grounding Systems | East Side Receipt Offload Scully Groundhog |  | Scully | ST-47-ELK | ST-47-ELK | 0 | 0 | X | 9-1.6.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | Bowser Offload Skid |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | West Side Offload Skid |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | East Side Skid |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | East Side Receipt Offload Ground Reel - South |  | Hannay | HGR-50-50 | 50 Feet | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | East Side Receipt Offload Ground Reel - North |  | Hannay | HGR-50-50 | 50 Feet | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | West Side Ground Reel on Skid |  | Hannay | JGR-50-50 | 50 Feet | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | West Side Offload Ground Reel 2 |  | Hannay | HGR 50-50 | 50 Feet | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Static Grounding Systems | West Side Offload Ground Reel 1 |  | Mil-Spec | Not Labeled | Not Labeled | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Electric Motors | East Side Receipt Offload Motor |  | Baldor Reliance | A1110312052 | 40CAMB-CONT 75C RISE | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Electric Motors | West Side Skid |  | Leeson | A6C34XC308 | 2 HP | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Electric Motors | West Side Offload |  | Baldor Reliance | A32-1144-0449 | 3555 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 11104 | Offload Pad / Canopy | Offload Pad | Lighting | Canopy |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact |  | 12 total
| 11104 | Offload Pad / Canopy | Offload Pad | Lightning Protection Systems | Canopy |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact |  | No lightning protection
| 11105 | Oil Water Separator | Oil Water Separator | Oil/Water Separators | Oil Water Separator |  | Highland Tank & Manufacturing Co. | Not Labeled | N/A | X | X | X | 11-5 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11105 | Oil Water Separator | Oil Water Separator | Centrifugal Pumps | OWS Pump 2 |  | Borger | PL 200 | GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11105 | Oil Water Separator | Oil Water Separator | Centrifugal Pumps | OWS Pump 1 |  | Borger | PL 200 | GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact
| 11105 | Oil Water Separator | Oil Water Separator | Aboveground Piping and Equipment Coatings | OWS Suction and Discharge Lines |  | N/A | N/A | 6.0 in. | X | X | 0 | 6-10.1 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 11105 | Oil Water Separator | Oil Water Separator | Gate Valves | OWS Pump 1 |  | Nibco 0-111-NO | 40186 | 4.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Gate Valves | OWS Inlet Line |  | Confined Space | Not Accessible | 4.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Ball Valves | OWS Pump 2 High Point |  | Nibco | Not Labeled | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11105 | Oil Water Separator | Oil Water Separator | Ball Valves | OWS Pump 1 High Point |  | Nibco | Not Labeled | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11105 | Oil Water Separator | Oil Water Separator | Check Valves | OWS Pump 2 |  | Nibco O-110-NO | 40183 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Check Valves | OWS Pump 1 |  | Nibco | 40013 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Motor Controls | OWS Pumps 1/2 |  | Highland Tank & Manufacturing Co. | Not Labeled | Not Labeled | X | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Panelboards | OWS Control Panel |  | Highland Tank & Manufacturing Co. | N/A | N/A | X | X | X | 9-1.5 | No Manufacturer Requirements Available | Quarterly - Verify that there are no physical obstructions blocking access to the panelboard. Remove physical obstructions. | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Electric Motors | OWS Pump 2 |  | WEG | 14303639 | 1750 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Electric Motors | OWS Pump 1 |  | WEG | 1053106456 | 1750 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS
| 11105 | Oil Water Separator | Oil Water Separator | Containment Systems | OWS Containment |  | N/A | N/A | N/A | 0 | 0 | X | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11107 | Fillstands | Fillstands | Fuel Truck Containment Areas | Canopy 11107 Containment Area |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 11107 | Fillstands | Fillstands | Canopies | Canopy 11107 |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11107 | Fillstands | Fillstands | Emergency Eyewash/Showers | Fillstand Northeast Corner |  | Haws | Not Listed | 2.0 In. | X | X | X | 11-3 | Weekly - Equipment installed within 10 seconds from the hazard and on the same plane as the hazard Pathway is clear of obstructions Plumbed equipment activated to ensure compliant operation and to clear any sediment Self-contained equipment checked to determine if the flushing fluid needs to be changed or supplemented Equipment free of broken or missing parts Equipment protected against freezing User protected from scalding water | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Signage and Markings | Canopy 11107 Signage |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11107 | Fillstands | Fillstands | Positive Displacement Meters | Fillstand 3 Issue Meter |  | Liquid Controls | M-60-2 | 60-600 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 11107 | Fillstands | Fillstands | Positive Displacement Meters | Fillstand 2 |  | Liquid Controls | M-60-2 | 600 GPM GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 11107 | Fillstands | Fillstands | Refuel Control Valves | Fillstand 3 |  | Cla-Val | 4-150 | 4.0 in. | X | X | 0 | 4-3.2.5 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Refuel Control Valves | Fillstand 2 |  | Cla-Val | 141225 | 4.0 in. | X | X | 0 | 4-3.2.5 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Pressure Control Valves | Fillstand 2 DBBV |  | Cla-Val | 8406602K | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | 20-200
| 11107 | Fillstands | Fillstands | Pressure Control Valves | Fillstand 3 |  | Cla-Val | 8106602K | 0.5 in. | X | X | 0 | 4-4.2.7 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Fixed Pantographs | Fillstand 2 |  | Cavotec Meyerinck | ME-9953-6090-1900337-28 | 3.0 In. | X | X | 0 | 4-7.1.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11107 | Fillstands | Fillstands | Fixed Pantographs | Fillstand 3 |  | Cavotec Meyerinck | ME-9501-5007-04 | 3.0 In. | X | X | 0 | 4-7.1.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 11107 | Fillstands | Fillstands | Fueling Nozzles | Fillstand Fueling Nozzle |  | Eaton | D-3 | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS
| 11107 | Fillstands | Fillstands | Fueling Nozzles | Fillstand 2 |  | Cla-Val | Eaton | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS
| 11107 | Fillstands | Fillstands | Aboveground Piping | Fillstand 3 |  | N/A | N/A | 4.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11107 | Fillstands | Fillstands | Aboveground Piping | Fillstand 2 PRV Piping |  | N/A | N/A | 1.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2 DBBV |  | Not Legible | Not Legible | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | DBBV / PCV / Isolation |  | Flo-Tite | CF8M | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2 PRV Isolation Valve |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2 Sample Cock |  | GTP | GTP-1149 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 3 Pressure Relief Isolation M-204 NO |  | Flo-Tite | 1-150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2 Gauge Isolation |  | Flo-Tite | F150 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2/3 Test port between PRVs |  | Merit | V210FP-16 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2 PRV Isolation 196 N/O |  | Flo-Tite | F150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 3 Pressure Gauge Isolation Valve M-202 NO |  | Flo-Tite | 1-150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 3 Sample Port |  | Flo-Tite | 1/4-150 | 0.25 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 3 M-199-NO |  | Flo-Tite | 1/2-150 | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 3 Double Block and Bleed Isolation Valve M-201-NC |  | Micro Fine | 3/4-150 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 3 Double Block and Bleed Isolation Valve M-200-NO |  | Micro Fine | 3/4-150 | 0.75 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2/3 Isolation Valve |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | RPTFR Seat
| 11107 | Fillstands | Fillstands | Ball Valves | Fillstand 2 DBBV |  | Not legible | Not legible | 0.5 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Ball Valves | Pressure Relief Isolation Valve M-203 NO |  | Flo-Tite | 1-150 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Double Block and Bleed Valves | Fillstand 2 /97N/O |  | Franklin Valve | D711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Double Block and Bleed Valves | Fillstand 3 M-94-NO |  | Franklin Valve | D711 | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Thermal and/or Pressure Relief Valves | Fillstand 3 Discharge side |  | Taylor | T-7700-1 | 1.0 in. 30 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11107 | Fillstands | Fillstands | Thermal and/or Pressure Relief Valves | Fillstand 2 |  | Taylor | T-7700-1 | 1.0 in. 30 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11107 | Fillstands | Fillstands | Pressure and Pressure/Vacuum Gauges | Fillstand 2 |  | Ashcroft | Duragauge | 0.25 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11107 | Fillstands | Fillstands | Pressure and Pressure/Vacuum Gauges | Fillstand 3 Discharge Pressure Gauge |  | Tube & Socket | AISI 316 | 1.0 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 11107 | Fillstands | Fillstands | EFSO Systems | Fillstand 2/3 Emergency Fuel Shutoff |  | Not Labeled | Not Labeled | Not Labeled | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Static Grounding Systems | Fillstand 3 Ground between Gate Valve and Control Valve |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Static Grounding Systems | Fillstand 2 Piping |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS
| 11107 | Fillstands | Fillstands | Lighting | Canopy 11107 Lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 11107 | Fillstands | Fillstands | Electronic Overfill Protection Systems | Fillstand 3 Scully Intellitrol |  | Scully | Intellitrol | Intellitrol | X | X | 0 | 9-6 | Proof Test : Confirm that the control module is indicating a dry condition (output relay closed). Bypass the safety function and take appropriate action to avoid a false trip Remove power from the WX system relay. Confirm that the relay opens within one (1) second. Reconnect power. Disconnect one of the wires to the sensor. Confirm that the relay opens within one (1) second. Reconnect power. Short the two sensor wires together. Confirm that the relay opens within one (1) second. Remove short. Remove the bypass and otherwise restore normal operation | No Operator Requirement | Partial System OOS | CMP
| 11107 | Fillstands | Fillstands | Electronic Overfill Protection Systems | Fillstand 2 |  | Scully | Intellitrol | Intellitrol | X | X | 0 | 9-6 | Proof Test : Confirm that the control module is indicating a dry condition (output relay closed). Bypass the safety function and take appropriate action to avoid a false trip Remove power from the WX system relay. Confirm that the relay opens within one (1) second. Reconnect power. Disconnect one of the wires to the sensor. Confirm that the relay opens within one (1) second. Reconnect power. Short the two sensor wires together. Confirm that the relay opens within one (1) second. Remove short. Remove the bypass and otherwise restore normal operation | No Operator Requirement | Partial System OOS | CMP
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Aboveground Piping | Piping Outside of Containment |  | N/A | N/A | 10.0 in. | X | X | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Issue Line Pressure Relief Isolation Valve |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Issue Line Pressure Relief Isolation Valve |  | Flow-Tek | RF15-1 | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Issue Line Pressure Relief Isolation Valve |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Issue Line Pressure Relief Isolation Valve |  | Flow-Tek | CF8M | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Receipt Line High Point Drain Valve |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Painted over
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Issue Line High Point Drain Valve |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Hydrant Return Line High Point Drain Valve |  | Painted Over | Painted Over | 1.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Ball Valves | Receipt Line Low Point Drain Valve |  | Painted Over | Painted Over | 2.0 in. | X | 0 | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Double Block and Bleed Valves | Issue Line Double Block and Bleed Valve O-F-NC |  | Duraseal | D711 | 16.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Double Block and Bleed Valves | Issue Line Double Block and Bleed Valve O-E-NC |  | Duraseal | D711 | 16.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Coming out of dike at Tank 11101
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Thermal and/or Pressure Relief Valves | Issue Line Pressure Relief Valve |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
| 11535 | Piping / Outside of Dike | Piping / Outside of Dike | Thermal and/or Pressure Relief Valves | Issue Line Pressure Relief Valve |  | Taylor | T-8200-1 | 1.0 in. 26 - 50 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be inspected for signs of leaks. Inspect valve exterior of thermal and pressure relief valves for corrosion. Repaint as required. Adjustment not reccomended. | Monthly for Army, Navy, USMC; Quarterly for AF - Thermal and pressure relief valves shall be inspected for signs of leak-by. Inspect relief valves for leaks by visually inspecting downstream flow indicators (if installed) for flow. If no flow indicators are installed listen for possible leaks. If suspect: isolate and test the relief valve; check opening pressure; and verify re-seating. Malfunctioning valves shall be repaired or replaced. Monthly for Army, Navy, USMC; Quarterly for AF - Ensure manual isolation valves installed upstream and downstream of thermal and pressure relief valves are open with valve handles are removed, wired open or locked. | Partial System OOS
Instructions:
1. Input all data as indicated on the sheet.
2. Additional documents referred to in the Special Considerations column shall be included as an appendix to this FMP.
3. The contractor shall generate a Component Unique Identifier (CUID) for each component utilizing the Component Acronym Sheet within this Work Book. The unique identifier must use the following:
Three letter Site Code - Facility # - Component Acronym - Sequential number
Example: AAD-00063A-RCVL-0001
If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment. Base Asset ID if used by site shall be cross referenced with CUID appropriately.
4. Utilize the UFC Section Reference Work Category as noted on the Component Acronym Sheet.
5. Enter any applicable manufacturer requirements not stated in the UFC. References are acceptable with attachments.
6. Enter any applicable operator support or government owned equipment required to complete the RM task.
7. Enter impact on system availability by performing the RM task. This could include shutdown, lockout, or similar impacts.
8. Enter contract information for any other contract, contractor, or government personnel performing the applicable task. This is applicable to other Centrally Managed Programs, SRM, MILCON, or Public Works/Civil Engineering projects.
9. Print Hard Copies as 11x17.

## FS-PF Schedule
FILTER SEPARATOR/PRE-FILTER MAINTENANCE SCHEDULES
Applicable Facility Assets | [10 empty] | Coalescer/Separator Information | [7 empty] | Special Considerations
Real Property Unique Identifier (RPUID) | Real Property Facility # | Real Property Facility Name | Operational Area | Component Type | Base Asset ID | Component Unique Identifier (CUID) | Make | Model | Capacity (GPM) | UFC Section Reference | Number of Coalescer Cartridges | Number of Separator Cartridges | Coalescer Cartridges Model # | Separator Cartridge Model # | Clean or Replace Separator Cartridge | Gasket Model # | Date Last Replaced | Replacement Due Date | Operator/Equipment Requirements | System Availability | Site Self Performs (Y/N) | Comments
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Receipt Separator |  | Facet | VCS-1243-436 | 1,200 GPM GPM/SCFM 100 Gallons | 3-6.2 | 12 | 4 | SEPTSM100-36FF-5 | CM100-435B-5 | Cleaned, as its required | 102930 |  | 2021-08-01 |  |  | Y | Site does their own filter changes
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Issue Pump 2 Filter Separator |  | Facet | VCD-643-236 | 600 GPM GPM/SCFM 100 Gallons | 3-6.2 | 6 | 2 | SM100-36FF-5 | CM100-435B-5 | Cleaned, as its required | 100948 |  | 2020-09-01 |  |  | Y | Site does their own filter changes
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Issue Pump 1 Separator 1 |  | Facet | VCS-643-236 | 600 GPM GPM/SCFM Gallons | 3-6.2 | 6 | 2 | SM100-36FF-5 | CM100-435B-5 | Cleaned, as its required | 100948 |  | 2021-08-01 |  |  | Y | Site does their own filter changes
| 981 | Issue Pad / Canopy | Issue Pad / Canopy | Filter Separators | Issue line 3 separator |  | Facet | VOS-643-256 | 600 GPM GPM/SCFM Gallons | 3-6.2 | 6 | 2 | SM100-36FF-5 | CM100-435B-5 | Cleaned, as its required | 100948 |  | 2021-10-01 |  |  | Y | Site does their own filter changes
| 982 | Receipt Pad / Canopy | Receipt Pad | Filter Separators | F/S 2B |  | Facet | VCS-643-236 | 600 GPM GPM/SCFM 100 Gallons | 3-6.2 | 6 | 2 | SM100-36FF-5 | CM100-435B-5 | Cleaned, as its required | 100948 |  | 2021-10-01 |  |  | Y | Site does their own filter changes
| 982 | Receipt Pad / Canopy | Receipt Pad | Filter Separators | F/S 2A |  | Facet | VCS-643-236 | 600 GPM GPM/SCFM 300 Gallons | 3-6.2 | 6 | 2 | SM100-36FF-5 | CM100-435B-5 | Cleaned, as its required | 100948 |  | 2022-01-01 |  |  | Y | Site does their own filter changes
Instructions:
1. Input all data as indicated on the sheet.
2. Additional documents referred to in the Special Considerations column shall be included as an appendix to this FMP.
3. The contractor shall generate a Component Unique Identifier (CUID) for each component utilizing the Component Acronym Sheet within this Work Book. The unique identifier must use the following:
Three letter Site Code - Facility # - Component Acronym - Sequential number
Example: AAD-00063A-RCVL-0001
If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment.
4. Utilize the UFC Section Reference Work Category as noted on the Component Acronym Sheet.
5. Enter any applicable manufacturer requirements not stated in the UFC. References are acceptable with attachments.
6. Enter any applicable operator support or government owned equipment required to complete the RM task.
7. Enter impact on system availability by performing the RM task. This could include shutdown, lockout, or similar impacts.
8. Filter Separators and Pre-Filters identified here shall also be provided in the Task Matrix Tab.
9. Print Hard Copies as 11x17.

## Component Acronym
Component Unique Identifier: | Site Code-Facility #-Component Acronym-Sequential #
Example: | AAD-00063A-RCVL-0001
NOTE: If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment
DLA Work Type Category | UFC Section Reference Work Category (Revised per Change 1, 29 April 2021) | Component Acronym
Air Compressors | Air Compressors | AIRC
Alarms | Externally Mounted Level Alarms (Section 8-9.9.1) | EMLA
| Internally Mounted Level Alarms (Section 8-9.9.3) | IMLA
Bollard | Bollards | BLRD
Building | Building HVAC | BHVAC
| Building Domestic Water System | BWTR
| Building Waste Water | BWSW
| Building - Lighting | BLTG
| Building - Architectural | BARCH
| Building - Fire Sprinkler System | BFIRE
Containment/Joints | Containment Systems (General) (Section 8-10.1) | CSGEN
| Concrete and Cement Brick Dike/Berm Walls (Section 8-10.2.1) | DKBW
| Dike/Berm Floors (Section 8-10.2.2) | DKBF
| Earthen Dike Walls (Section 8-10.3) | ETHDW
| Self-Diking or Vaulted Tank Containment (Section 8-10.4) | SDVTCS
| Flexible Membrane Liners (Section 8-10.5) | FXML
| Fuel Truck and Rail Car Containment Areas (Section 11-1.1) | FTKRCC
| Remote Spill Containment (Section 11-1.2) | RSCS
| Piers and Wharves Fuel Containment Systems (Section 5-1.2) - Testing | FPWCT
| Fuel Pier/Wharf Containment (PWS Section 3) | FPWC
Corrosion Control/Coatings | Aboveground Piping and Equipment Coatings (Section 6-10.1) | AGPCT
Miscellaneous | Miscellaneous Deactivated Components (Section 12-5) | MDEAC
Electrical/Lighting | Lighting (Section 9-1.8) | LIGHT
Electrical/Power | Electrical Equipment (Section 9-1.2) | ELEQ
| Power Cables (Section 9-1.3) | PWRCBL
| Motor Controls (Section 9-1.4) | MTRCT
| Panelboards (Section 9-1.5) | PNLB
| Electric Motors (Section 9-1.7) | ELEMT
| Electronic Equipment (9-1.9) | ELTREQ
| Card and Key Locks (Section 9-3) | CKLK
Electrical/Protection | Power Grounding Systems (Section 9-1.6.1) | PWRGS
| Static Grounding Systems (Section 9-1.6.2) | STGS
| Cathodic Protection (Section 9-2.1) | CP
| Lightning Surge Arresters (Section 9-2.2.1) | LSAR
| Lightning Protection Systems (Section 9-4) | LPTS
| Ground Verification System (Section 9-5) | GRVS
| Electronic Overfill Protection Systems (Section 9-6) | EOPS
Eyewash/Shower | Emergency Eyewash/Showers (Section 11-3) | EMEWSH
Fencing/ Gates | Fencing | FENC
| Gates | GATE
Filtration | Pre-Filters (Section 3-6.1) | PFVSL
| Filter Separators (Section 3-6.2) | FLSP
| Haypack Filters (Section 3-6.3) | HPKF
| Basket Strainers (Section 3-6.4) | BSTR
| Filter Separator Sump Heaters (Section 3-6.5) | FSSH
| Sidestream Filtration Systems (Section 8-9.11) | SSFTS
Fire Suppression Equipment | Flame Arrestors (Section 8-9.5) | FLMARR
| Foam Fire Protection Systems (Section 8-9.15) | FFPS
| Fire Protection Systems - Wet Pipe | FPRS
Fuel Laboratories | Ventilation Hoods (Section 11-4.1) | VENTHD
Gauges | Pressure and Pressure/Vacuum Gauges (Section 6-7.1) | PVGA
| Differential Pressure Gauges (Section 6-7.2) | DPGA
| Mechanical Tape Gauges (Section 8-9.7) | MTGA
| Mechanically Operated Tape Gauge (Section 8-9.8.1) | MOTGA
| Magnetostrictive Probes (Section 8-9.8.2) | MRPRB
| Servo Gauge (Section 8-9.8.3) | SRVGA
Generators | Back-Up Power Generators | BGEN
Heating Coils | Steam Type Heating Coils (Section 8-9.16.1) | STHC
| Thermal Fluid Type Heating Coils (Section 8-9.16.2) | TFTHC
| Electric Rod Type Heating (Section 8-9.16.3) | ERTH
Hoses | Loading Fuel Hoses (Section 3-9.1) | LDHS
| Offloading Fuel Hoses (Section 3-9.2) | OLHS
| Aircraft Fueling Hoses (Section 4-7.5) | ACFHS
Hydrazine | Hydrazine Charging Units (Section 10-3) | HDZCU
Inspections | Trouble Shoot | TRBST
| API 510 Inspections | API510
| API 653 or STI Inspection | API653
| Coatings Condition Survey | CCS
Issue/Receive - Ground | Dispenser Nozzles (Section 7-2) | DSNZ
| Dispenser Hoses (Section 7-3) | DSHS
| Breakaways (Section 7-4) | DSBW
| Swivels (Section 7-5) | DSSW
| Hose Retriever (Section 7-6) | HSRTV
| Dispenser Cabinet (Section 7-7) | DSCB
| Dispenser Meters (Section 7-8) | DSMTR
| Dispenser Filters (Section 7-9) | DSFLR
| Dispenser Strainers (Section 7-10) | DSSTR
| Ground Vehicle Fuel Piping (Section 7-11) | GVFP
| Emergency Shutoff Valves (Shear Valves) (Section 7-12) | ESHVL
| Dispenser Sumps (Section 7-13) | DSSMP
| Transition Sumps (Section 7-14) | TRSMP
| Remote Dispenser Pumps (Section 7-15.1) | RDSP
| Self-Contained Dispenser Pumps (Section 7-15.2) | SCDSP
| EFSO Systems (Section 7-16) | EFSO
| Stage I Vapor Recovery (Section 7-17.1) | SIVP
| Stage II Vapor Recovery (Section 7-17.2) | SIIVP
| Vapor Burners (Section 7-17.3) | VPBNR
| Point Sensor - Dry (Section 7-19.1.1) | PSDRY
| Automatic Line Leak Detector (Section 7-19.1.2) | ALLD
| Visual Monitoring (Section 7-20.1) | VSLM
Issue/Receive - Marine | Marine Receipt (Section 5-2) | MRNRCP
| Marine Issue (Section 5-3) | MRNISU
| Marine Loading Arms (Section 5-4) | MRNLA
| Marine Transfer Hoses (Section 5-5.1) | MBTHS
| Underwater Hoses (Section 5-5.2) | UWHS
| Single Point Mooring Systems (Section 5-7.1) | SPMSS
| Multi Point Mooring Systems (Section 5-7.2) | MPMSS
| Submerged Piping Systems (Section 5-8) | SMPS
| Boom Reels (Section 5-9) | BMRL
Liquefied Petroleum | Liquefied Petroleum Tanks (Section 10-1.1) | LPTANK
| Liquefied Petroleum Pipelines (Section 10-1.2) | LPPIPE
| Liquefied Petroleum Vapor Lines (Section 10-1.3) | LPVPL
| LPG Vaporizers (Section 10-1.4) | LPGVPZ
| Petroleum Gas Regulators (Section 10-1.5) | PGREG
| Liquefied Petroleum Gas Hoses (Section 10-1.6) | LPGHS
Meter/ calibrations | Positive Displacement Meters (Section 3-7.1) | PDMT
| Turbine Flow Meters (Section 3-7.2) | TBFMT
| Orifice Flow Meters (Section 3-7.3) | OFMT
Natural Disaster | Natural Disaster
Natural Gas | CNG Piping (Section 10-2.1) | NGPIPE
| CNG Compressors (Section 10-2.2) | NGCOMP
| CNG Storage (Section 10-2.3) | NGSTOR
| CNG Dispensers (Section 10-2.4) | NGDS
| CNG Dispenser Hoses (Section 10-2.5) | NGDSHS
Nozzle | Hydrant Adapters (Section 4-7.2) | HADP
| Fueling Nozzles (Section 4-7.3) | FLNZ
Other | Fuel Additive Injectors (Section 3-11) | FAIJ
Pantograph | Fixed Pantographs (Section 4-7.1.1) | FXPNT
| Detachable Pantographs (Section 4-7.1.2) | DTPNT
Piping | On-Base Pipelines (Section 6-1.1) | OBPL
| Non-DOT Regulated (Section 6-1.2.1) | NDPL
| Aboveground Piping (Section 6-1.3) | AGPL
| Double-Wall Piping (Section 6-1.4) | DWPL
| Low Point Drains (Section 6-12.1) | LPDN
| High Point Vents (Section 6-12.2) | HPVT
| Sight Flow Indicators (Section 6-12.3) | SFND
| Rope Sensor Systems (Section 6-13.1.1) | RPSS
| Point Sensor - Dry (Section 6-13.1.2) | PSDRY
| Visual Monitoring (Section 6-14.1) | VSLM
| Pipe Penetrations (Section 8-10.6) | PPEN
| Deactivated Petroleum Fuel Pipelines (Section 12-3) | DEACPL
Pressure/Temperature Control | Air Eliminator Tanks (Section 3-10.1) | AELT
| Automatic Air Vents (Section 3-10.2) | AAVT
| Surge Suppressors (Section 4-7.4) | SRGSP
| Thermal and Pressure Relief Valves (Section 6-6.3) | TPRVL
| Pressure Transmitters (Section 6-7.3) | PRTR
| Differential Pressure Transmitters (Section 6-7.4) | DPTR
| Flexible Ball Joints (Section 6-8) | FBLJT
| Dial Thermometer (Section 6-9.1) | DTHMR
| Emergency Vents (Section 8-9.4) | EMGVT
Pump | Centrifugal Pumps (Section 3-8.1) | CENP
| Vertical Inline Pumps (Section 3-8.2) | VILP
| Vertical Turbine/Submerged Turbine Pumps (Section 3-8.3) | VTSP
| Sliding Vane Pumps (Section 3-8.5) | SLVP
| Gear Pumps (Section 3-8.6) | GERP
| Diaphragm Pumps (Section 3-8.7) | DIAP
| Internal Combustion Drives (Section 3-8.8) | ICDR
| Gearboxes (Section 3-8.9) | GRBX
| Deactivated Petroleum Fuel Pumps (Section 12-4) | DEACP
Signage/Markings | Signage and Markings (Section 2-7) | SIGN
Structures | Pumphouse/Filter Buildings (Section 11-2.1) | PFBLDG
| Canopies (Section 11-2.2) | CNPY
| Cranes and Hoists (Section 11-6) | CRNHST
Tank | Aboveground Field-Erected Tanks (Section 8-4) | AGFET
| Geodesic Dome Roofs (Section 8-4.2) | GEODR
| Foundations (Section 8-4.3) | FOUND
| Aboveground Shop Fabricated Tanks (Section 8-5.1) | AGSFP
| Self-Diking or Vaulted Tanks (Section 8-5.2) | SDVT
| Rectangular Concrete-Encased Tanks (Section 8-5.3) | RCET
| Single-Walled Underground Shop-Fabricated Tanks (Section 8-5.4.1) | UGSSFT
| Double-Walled Underground Shop-Fabricated Tanks (Section 8-5.4.2) | UGDSFT
| Underground Field-Constructed Tanks (Cut and Cover Tanks) (Section 8-6) | UGFET
| Tank Cleaning (Section 8-7) | TCLEAN
| Aluminum Honeycomb Floating Pans (Section 8-9.1.1) | AHFP
| Steel Floating Pans (Section 8-9.1.2) | STLFP
| Pontoon Floating Pans (Section 8-9.1.3) | PTNFP
| Floating Roofs (Section 8-9.1.4) | FLTRF
| Floating Roof and Pan Pressure/Vacuum Vents (Section 8-9.1.5) | FPPVV
| Floating Roof and Pan Legs (Section 8-9.1.6) | FRPLG
| Secondary Tank Bottoms (Section 8-9.2) | SNDTB
| Tank Pressure/Vacuum Vents (Section 8-9.3) | TPVVT
| Product Saver Tanks (Section 8-9.10) | PRDST
| Fill Ports (Section 8-9.12) | FPRT
| Point Sensor - Dry (Section 8-9.13.1) | PSDRY
| Point Sensor - Wet (Section 8-9.13.2) | PSWET
| Point Sensor - Pressure/Vacuum (Section 8-9.13.3) | PSPV
| Visual Leak Detection (Section 8-9.13.4) | VSLLD
| Floating Suction Lines (Section 8-9.14) | FLTSL
| Stilling Wells (Section 8-9.17) | STGW
| Deactivated Petroleum Fuel Tanks (Section 12-2) | DEACT
Testing | Pressure Testing
Underground Pits | Isolation Valve Pits (Section 6-11.1) | ISVLP
| Hydrant Fuel Pits (Section 6-11.2) | HDFP
| High Point Vent Pits (Section 6-11.3) | HPVP
| Low Point Drain Pits (Section 6-11.4) | LPDP
| Lateral Control Pits (Section 6-11.5) | LTCP
Valves | General System Control Valves (Section 4-3.2.1) | GSCVL
| Refuel Control Valves (Section 4-3.2.5) | RCVL
| Pressure Relief Valves (Section 4-3.2.6) | PRCVL
| Defuel Control Valve (Section 4-3.2.7) | DFCVL
| Dual Rate-of-Flow Control Valves (Section 4-3.2.8) | DRFCVL
| Combination Dual Rate-of-Flow Control and Solenoid Valves (Section 4-3.3.1) | CFSCVL
| Dual Pressure Relief, Solenoid Shutoff, and Check Valves (Section 4-3.3.2) | DPSCVL
| Non-Surge Check Valves (Section 4-4.2.1) | NSCKVL
| Filter Separator Control Valves (Section 4-4.2.2) | FSCVL
| Defuel/Flush Valves (Section 4-4.2.3) | DFFCVL
| Issue Venturi (Section 4-4.2.4) | ISVTR
| Return Venturi (Section 4-4.2.5) | RTVTR
| Back Pressure Control Valves (Section 4-4.2.6) | BPCVL
| Pressure Control Valves (Section 4-4.2.7) | PCVL
| Hydrant Control Valves (Section 4-4.2.8) | HCVL
| Emergency Shut-off Valves (Section 4-4.2.9) | ESOVL
| Pantograph Control Valves (Section 4-5.2.12) | PTCVL
| Pantograph Pressure Control Valves (Section 4-5.2.13) | PTPCVL
| Overfill Valve for Product Recovery Tanks (Section 4-8.1) | OVLPRT
| Plug Valves - Lubricated (Section 6-6.2.1) | PLVL
| Plug Valves - Non-lubricated (Section 6-6.2.2) | NPLVL
| Gate Valves (Section 6-6.2.3) | GTVL
| Ball Valves (Section 6-6.2.4) | BLVL
| Double Block and Bleed Valves (Section 6-6.2.5) | DBBVL
| Butterfly Valves (Section 6-6.2.6) | BFVL
| Globe Valves (Section 6-6.2.7) | GLVL
| Check Valves (Section 6-6.2.8) | CKVL
| Line Blanks, Ring Spacers, and Spectacle Blinds (Section 6-6.2.9) | BLIND
| Manual Valve Gear Operators (Section 6-6.2.10) | MVLGO
| Fire Valves (Section 6-6.4.1) | FRVL
| Fusible Link Butterfly Valves (Section 6-6.4.2) | FLBFVL
| Truck Fill Valves (Section 6-6.5.1) | TFVL
| Motor Operators (Section 6-6.6) | MTROP
| External High Level Shutoff Valves (HLSO) (Section 8-9.6.1) | EHLSVL
| Internal HLSO Valves (Section 8-9.6.2) | IHLSVL
Waste | Oil/Water Separators (Section 11-5) | OWS

## Versions and Notes
Version | Date | Description of changes
v2.0 | 2021-08-18 | Updated Task Matrix to meet UFC 3-460-03 Change 1 , 29 April 2021
Updated Component Acronym Tab to meet UFC 3-460-03 Change 1 , 29 April 2021
v2.1 | 2022-04-20 | Task Matrix Tab - Deleted all services facility # columns and combined into one. Renamed "Real Property Facility #"
Task Matrix Tab - Added "RPUID" to Real Property Unique Identifier column
Task Matrix Tab - Added "Real Property" to Facility Name
Task Matrix Tab - Added column for "Base Asset ID"
Task Matrix Tab - Added "Additional" and "RM" to Manufacturer Requirements
Task Matrix Tab - Changed Comment note for Filter Separator
Task Matrix Tab - Changed Note #3 To add "Base Asset ID if used by site shall be cross referenced with CUID appropriately."
Task Matrix Tab - Changed note #7 under instructions for Task Matrix to clarify this column
Task Matrix Tab - Changed note #8 under instructions for Task Matrix to clarify this column
Added new tab for RM schedule to be included
Added new Tab for Filter Separator/Pre-Filter Schedule with instructions
Administrative Tab - changed Installation to Site and added Site Code to comply with new requirements as the three letter DLA site code is obsolete
General Facility Description - Changed the Instructions
Reversed columns 'Base Asset ID' and 'CUID' to match RM report for all tabs
Added FMP version to footer
v2.2 | 2022-10-31 | Administrative Tab - Added rows for POC Name for all
Administrative Tab - Added RPSUID in cell B2
General Facility Description Tab - Added "fuel type"
Communication Plan Tab - added "coordination for access"
Safety Tab - Changed instructions to read "Site Specific Addendum and Activity Hazard Analysis, which are Attachments to the APP, specific to activities or tasks related to recurring maintenance for this site."
Changed footer for tabs to FMP v2.2
Task Matrix and FS/PF Schedule added not to print as 11x17. Also changed in page layout.