## Administrative
Location | Site Name | Lexington AASF No 1
| RPSUID | 5890
| DLA Site Code | LEX
| Hours of Operation | 0800-1600
| Address | 16201 144th St, Lexington, OK 73051
Contract | Contractor
Contract #
Local POCs | QAE Name
QAE Phone
QAE Email
Alt QAE Name
Alt QAE Phone
Alt QAE Email
DLA/SCP POCs | DLA PM Name
DLA PM Phone
DLA PM Email
SCP PM Name
SCP PM Phone
SCP PM Email
Contractor POCs | Contractor PM Name
Contractor PM Phone
Contractor PM Email
Contractor QC Name
Contractor QC Phone
Contractor QC Email
Contractor SM Name
Contractor SM Phone
Contractor SM Email
USACE POCs | USACE PM/COR Name
USACE PM/COR Phone
USACE PM/COR Email
USACE PE Name
USACE PE Phone
USACE PE Email
USACE KO Name
USACE KO Phone
USACE KO Email
Instructions:
This table shows the minimum information required. Additional details should be included based on site specific requirements. Additional POCs may be required.

## General Facility Description
Facility Description
Purpose: This Facility Maintenance Plan provides guidance for Contractor personnel in the operation, inspection, and maintenance of permanently installed fuel facilities operated under the control of the Quality Assurance Evaluators. Federal, state, and local environmental laws and regulations shall be complied with if this plan is in conflict with them. Scope: The instructions prescribed by this plan outline general fuels maintenance information associated with fuel storage and dispensing systems and provides the minimum periodic contractor maintenance and inspection criteria requirements for the systems. This plan is to be used in conjunction with other existing directives governing fuel system operations and maintenance requirements. Conotractor will properly maintain and repair federally funded petroleum systems and facilities in order to provide compliance with applicable code, criteria, and federal, state, local and/or host nation regulations. Fuels Facilities: Organizational tanks, and associated dispensing equipment are maintained and operated by the owning organization. Fuel system maintenance contractors shall perform all maintenance and associated procurement actions on installed fuel systems. Each installation under the Southwest Division contract are military land-based facilities who receive, store, distribute, and/or dispense liquid fuels. Standard fuel system equipment includes: a) Above Ground Sorage Stanks (AST), Underground Storage Tanks (UST) b) Filter/separator and other filtration device maintenance access, particularly element removal. c) Manual valves d) Meter Registers, and Flow Meters. e) Control Valves. f) Pumps g) Tank Monitoring Equipment and Instruments h) Alarms i) Fire Fighting Equipment Site Specific General Information:
Instructions:
Include a general facility overview and description of each fuel system for the sites in accordance with UFC 3-460-01. Examples include: Bulk Storage Facilities, Aircraft Fueling Facilities, Marine and Dispensing Facilities, Ground Products Fueling Facilities, Alternate POL Facilities, and Support Facilities. Also include facility #s, facility names, fuel type, photos, and any other pertinent information.
Include Site Specific Conditions and Restrictions in this tab.

## Communication Plan
Instructions:
Communication plan shall address in/out briefs, lines of communication, coordination for access, etc.

## Safety
Instructions:
Site Specific Addendum and Activity Hazard Analysis, which are Attachments to the APP, specific to activities or tasks related to recurring maintenance for this site.

## RM Schedule
Instructions:
Link RM schedule here

## Task Matrix
Applicable Facility Assets | [9 empty] | UFC System Level Maintenance Frequency |  |  |  | Special Considerations
Real Property Unique Identifier (RPUID) | Real Property Facility # | Real Property Facility Name | Operational Area | Component Type | Base Asset ID | Component Unique Identifier (CUID) | Make | Model | Capacity/Size | Q | S | A | UFC Section Reference | Additional Manufacturer RM Requirements | Operator/ equipment Requirements | System availability | Other Contract | Comments
| 40C35 | FTKOA | Bulk Storage | Filter Separators | Issue Filter Separator 1 |  | Velcon | HV2838200 | 600 GPM | X |  |  | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Filter Seperator Control Valves | Filter Seperator Control Valves |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Refuel Control Valves | Filter Seperator Control Valves |  | Cla Val | M119 | 300 psi | X |  |  | 4-3.2.5 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Differential Pressure Gauges | Differential Pressure Gauges |  | Gammon | GTP-534-30S | 0-30 psi | X |  | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Loading Fuel Hoses | Issue Hose |  | Goodyear | API 1529 Type C | 10' X 3" | X |  | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Static Ground System | Ground Reel |  | Hannay | HGR100 | 3/16" x 100ft | X |  | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOA | Bulk Storage | Basket Strainer | Basket Strainer |  | Titan | 125 | 3" |  |  |  | 3-6.4 | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Partial System Impact if Required
| 40C35 | FTKOA | Bulk Storage | Positive Displacement Meter | Offload 1 |  | Veeder-Root | 0788700-063 | 30 - 600 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure and Vacuum Pressure Gauge |  | Ashcroft | Unknown | minus 30 to 300 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 - 100 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 - 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 - 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOA | Bulk Storage | Centrifugal Pumps | Issue Pump 1 |  | Goulds | 3196 | 300 GPM | X |  | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | Temporary System OOS
| 40C36 | FTKOA | Bulk Storage | Electric Motor | Issue Pump 1 |  | US Electrical | AB39E | 3535 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Temporary Mission Impact
| 40C35 | FTKOA | Bulk Storage | Motor Controls | Issue Pump 1 |  | Unknown | Unknown | Unknown |  | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE400 | Bulk Storage | Positive Displacement Meter | Issue 1 |  | Liquid Controls | M-42-2 | 45 - 450 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Filter Separators | Issue Filter Separator 2 |  | Velcon | HV2838200 | 600 GPM | X |  |  | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Filter Seperator Control Valves | Filter Seperator Control Valves |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Differential Pressure Gauges | Differential Pressure Gauges |  | Gammon | GTP-534-30S | 0-30 psi | 0.25 |  | 0.05 | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Loading Fuel Hoses | Issue Hose |  | Goodyear | API 1529 Type C | 10' X 3" | X |  | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Static Ground System | Ground Reel |  | Hannay | HGR100 | 3/16" x 100ft | X |  | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOD | Bulk Storage | Basket Strainer | Basket Strainer |  | Titan | 125 | 3" |  |  |  | 3-6.4 | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Partial System Impact if Required
| 40C35 | FTKOD | Bulk Storage | Positive Displacement Meter | Offload 2 |  | Veeder-Root | 0788700-063 | 30 - 600 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure and Vacuum Pressure Gauge |  | Ashcroft | Unknown | minus 30 - 300 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 to 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 to 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Pressure and Vacuum Pressure Gauge | Vacuum Gauge |  | Ashcroft | Unknown | minus 30 - 0 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOD | Bulk Storage | Centrifugal Pumps | Issue Pump 2 |  | Goulds | 3196 | 300 GPM | X |  | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | Temporary System OOS
| 40C36 | FTKOD | Bulk Storage | Electric Motor | Issue Pump 2 |  | US Electrical | AB39E | 3535 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Temporary Mission Impact
| 40C35 | FTKOA | Bulk Storage | Motor Controls | Issue Pump 2 |  | Unknown | Unknown | Unknown |  | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE400 | Bulk Storage | Positive Displacement Meter | Issue 2 |  | Liquid Controls | M-42-2 | 45 - 450 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Filter Separators | Receipt Filter Separator 1 |  | Velcon | HV2838200 | 600 GPM | X |  |  | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Filter Seperator Control Valves | Filter Seperator Control Valves |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Back Pressure Control Valves | Back Pressure Control Valves |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Differential Pressure Gauges | Differential Pressure Gauges |  | Gammon | GTP-534-30S | 0-30 psi | X |  | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Dixon | TTMA-Flanged | 4" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Offloading Fuel Hoses | Offloading hose |  | Hewitt | 500 | 4" x 10' | X |  | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Centrifugal Pumps | Reciept Pump 1 |  | Goulds | 3196 | 300 GPM | X |  | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | Temporary System OOS
| 40C36 | FTKOM | Bulk Storage | Electric Motor | Reciept Pump 1 |  | TECO | CAT X0302 | 3545 RPMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Temporary Mission Impact
| 40C35 | FTKOA | Bulk Storage | Motor Controls | Reciept Pump 1 |  | Unknown | Unknown | Unknown |  | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Temporary Mission Impact
| 40C35 | FTKOM | Bulk Storage | Static Ground System | Ground Reel |  | Hannay | HGR50 | 3/16" x 75ft | X |  | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 40C35 | FTKOM | Bulk Storage | Basket Strainer | Basket Strainer |  | Titan | 125 | 3" |  |  |  | 3-6.4 | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Partial System Impact if Required
| 40C35 | FTKOM | Bulk Storage | Positive Displacement Meter | Offload 3 |  | Veeder-Root | 0788700-063 | 30 - 600 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure and Vacuum Pressure Gauge |  | Ashcroft | Unknown | minus 30 - 300 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 to 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 to 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | FTKOM | Bulk Storage | Pressure and Vacuum Pressure Gauge | Vacuum Gauge |  | Ashcroft | Unknown | minus 30 - 0 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Positive Displacement Meter | Transfer/Recirculation 1 |  | Liquid Controls | M-10-2 | 15 - 150 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Filter Separators | Receipt Filter Separator 2 |  | Velcon | HV2838200 | 600 GPM | X |  |  | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Filter Seperator Control Valves | Filter Seperator Control Valves |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Back Pressure Control Valves | Back Pressure Control Valves |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Differential Pressure Gauges | Differential Pressure Gauges |  | Gammon | GTP-534-30S | 0-30 psi | X |  | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Dixon | TTMA-Flanged | 4" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Sight Flow Indicators | Sight Flow Indicators |  | Visi-Flow | 1400 Series | 1" |  |  |  | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Offloading Fuel Hoses | Offloading hose |  | Hewitt | 500 | 4" x 10' | X |  | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Centrifugal Pumps | Reciept Pump 2 |  | Goulds | 3196 | 300 GPM | X |  | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | Temporary System OOS
| 40C36 | LE401 | Bulk Storage | Electric Motor | Reciept Pump 2 |  | Toshiba | 0302XPEA21B-P | 3535 RMs | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Temporary Mission Impact
| 40C35 | FTKOA | Bulk Storage | Motor Controls | Reciept Pump 2 |  | Unknown | Unknown | Unknown |  | X | X | 9-1.4 | Moving parts should operate easily without excessive friction. Check operation of contactors and relays by hand, feeling for any binding or sticking. Look for loose pins, bolts, or bearings. If the control is dirty, it should be wiped or blown clean. Contact inspection. Check contacts for pitting and signs of overheating, such as discoloration of metal, charred insulation, or odor. Be sure contact pressure is adequate and the same on all poles; verify with manufacturer's specification. Watch for frayed flexible leads. Contact resistance testing. On essential controls, perform contact-resistance tests with a low-resistance ohmmeter on a regular basis. Proper contact resistance should be about 50 micro-ohms. Record readings for future comparison. This will indicate trends in the condition of contacts. Overload relay inspection. Overload relays should receive a thorough inspection and cleaning. You also should check for proper setting. | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE400 | Bulk Storage | Static Ground System | Ground Reel |  | Hannay | HGR50 | 3/16" x 75ft | X |  | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | No Mission Impact
| 40C35 | LE400 | Bulk Storage | Basket Strainer | Basket Strainer |  | Titan | 125 | 3" |  |  |  | 3-6.4 | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly | Partial System Impact if Required
| 40C35 | LE400 | Bulk Storage | Positive Displacement Meter | Offload 4 |  | Veeder-Root | 0788700-063 | 30 - 600 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure and Vacuum Pressure Gauge |  | Ashcroft | Unknown | minus 30 - 300 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 to 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Pressure and Vacuum Pressure Gauge | Pressure Gauge |  | Ashcroft | Unknown | 0 to 200 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Pressure and Vacuum Pressure Gauge | Vacuum Gauge |  | Ashcroft | Unknown | minus 30 - 0 psi | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS
| 40C35 | LE400 | Bulk Storage | Positive Displacement Meter | Transfer/Recirculation 2 |  | Liquid Controls | M-10-2 | 15 - 150 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | LE401 | Bulk Storage | Aboveground Shop Fabricated Tanks | Tank 1 |  | Steel Tank Institute | 12363 | 20,000 gallon |  |  | X | 8-5.1 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-2): Visually inspect for exterior signs of corrosion or coating deterioration. Visually inspect weld seams, tank-to-saddle connections, tank supports, tank anchors, foundation and anchor bolts, overfill valves and alarms, normal vents, emergency vents, leak detection probe or water/petroleum accumulation in the interstice on double-walled tanks, leaking valves, fittings, or components, spill containment systems and release prevention barriers. Leaking valves, fittings or components shall be repaired immediately or immediately removed from service and isolated to prevent further discharge. Any irregularities, (e.g., missing valve handles, bolts, nuts, screens) will be assessed for priority and repaired as soon as possible or as required depending on the nature of the defect (See Appendix E for an example of the STI SP001 Standard Monthly Inspection Checklist). Annually - Annual External Inspection (Identified as P in Table 8-2): A more detailed examination of the tank and appurtenances shall be performed on an annual basis (See Appendix E for an example of the STI SP001 Standard Annual Inspection Checklist). | No Mission Impact
| 40C35 | LE401 | Bulk Storage | Aboveground Piping | Piping |  | N/A | N/A | N/A |  |  | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission impact
| 40C35 | LE401 | Bulk Storage | Emergency Vents | Vent |  | Morrison Brothers | 244O | Unknown |  |  | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE401 | Bulk Storage | Flame Arrestors | Vent |  | Morrison Brothers | 351S & 748A | N/A |  |  | X | 8-9.5 | No Manufacturer Requirements Available | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE401 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE405 | Bulk Storage | Panel Boards | Panel Boards |  | Unknown | Unknown | Unknown | X |  | X | 9-1.5 | No Manufacturer Requirements Available | Quarterly - Verify that there are no physical obstructions blocking access to the panelboard. Remove physical obstructions. | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Signage and Markings | Signage/Markings |  | N/A | N/A | N/A |  |  |  | 2-7 | No Manufacturer Requirements Available | Monthly - Check permanent signs and markings for adequacy and readability. Repair or replace deteriorated or illegible signs and markings. | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Containment Systems (General) | Containment Systems (General) |  | N/A | N/A | N/A |  |  | X | 8-10.1 | No Manufacturer Requirements Available | Daily - Inspect containment systems for cleanliness, if accessible. | No Mission Impact
| 40C35 | LE405 | Bulk Storage | EFSO Systems | Emergency Stop (Issue) |  | Appleton | EDS2714 | N/A | X |  |  | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE405 | Bulk Storage | EFSO Systems | Emergency Stop (Receipt) |  | Appleton | EDS2714 | N/A | X |  |  | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE402 | Bulk Storage | Aboveground Shop Fabricated Tanks | Tank 2 |  | Steel Tank Institute | 12363 | 20,000 gallon |  |  | X | 8-5.1 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-2): Visually inspect for exterior signs of corrosion or coating deterioration. Visually inspect weld seams, tank-to-saddle connections, tank supports, tank anchors, foundation and anchor bolts, overfill valves and alarms, normal vents, emergency vents, leak detection probe or water/petroleum accumulation in the interstice on double-walled tanks, leaking valves, fittings, or components, spill containment systems and release prevention barriers. Leaking valves, fittings or components shall be repaired immediately or immediately removed from service and isolated to prevent further discharge. Any irregularities, (e.g., missing valve handles, bolts, nuts, screens) will be assessed for priority and repaired as soon as possible or as required depending on the nature of the defect (See Appendix E for an example of the STI SP001 Standard Monthly Inspection Checklist). Annually - Annual External Inspection (Identified as P in Table 8-2): A more detailed examination of the tank and appurtenances shall be performed on an annual basis (See Appendix E for an example of the STI SP001 Standard Annual Inspection Checklist). | No Mission Impact
| 40C35 | LE402 | Bulk Storage | Aboveground Piping | Piping |  | N/A | N/A | N/A |  |  | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission impact
| 40C35 | LE402 | Bulk Storage | Emergency Vents | Vent |  | Morrison Brothers | 244O | Unknown |  |  | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE402 | Bulk Storage | Flame Arrestors | Vent |  | Morrison Brothers | 351S & 748A | N/A |  |  | X | 8-9.5 | No Manufacturer Requirements Available | No Operator Requirement | Temporary Mission Impact
| 40C36 | LE402 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE403 | Bulk Storage | Aboveground Shop Fabricated Tanks | Tank 3 |  | Steel Tank Institute | 12363 | 20,000 gallon |  |  | X | 8-5.1 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-2): Visually inspect for exterior signs of corrosion or coating deterioration. Visually inspect weld seams, tank-to-saddle connections, tank supports, tank anchors, foundation and anchor bolts, overfill valves and alarms, normal vents, emergency vents, leak detection probe or water/petroleum accumulation in the interstice on double-walled tanks, leaking valves, fittings, or components, spill containment systems and release prevention barriers. Leaking valves, fittings or components shall be repaired immediately or immediately removed from service and isolated to prevent further discharge. Any irregularities, (e.g., missing valve handles, bolts, nuts, screens) will be assessed for priority and repaired as soon as possible or as required depending on the nature of the defect (See Appendix E for an example of the STI SP001 Standard Monthly Inspection Checklist). Annually - Annual External Inspection (Identified as P in Table 8-2): A more detailed examination of the tank and appurtenances shall be performed on an annual basis (See Appendix E for an example of the STI SP001 Standard Annual Inspection Checklist). | No Mission Impact
| 40C35 | LE403 | Bulk Storage | Aboveground Piping | Piping |  | N/A | N/A | N/A |  |  | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission impact
| 40C35 | LE403 | Bulk Storage | Emergency Vents | Vent |  | Morrison Brothers | 244O | Unknown |  |  | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE403 | Bulk Storage | Flame Arrestors | Vent |  | Morrison Brothers | 351S & 748A | N/A |  |  | X | 8-9.5 | No Manufacturer Requirements Available | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE403 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE404 | Bulk Storage | Aboveground Shop Fabricated Tanks | Tank 4 |  | Steel Tank Institute | 12363 | 20,000 gallon |  |  | X | 8-5.1 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-2): Visually inspect for exterior signs of corrosion or coating deterioration. Visually inspect weld seams, tank-to-saddle connections, tank supports, tank anchors, foundation and anchor bolts, overfill valves and alarms, normal vents, emergency vents, leak detection probe or water/petroleum accumulation in the interstice on double-walled tanks, leaking valves, fittings, or components, spill containment systems and release prevention barriers. Leaking valves, fittings or components shall be repaired immediately or immediately removed from service and isolated to prevent further discharge. Any irregularities, (e.g., missing valve handles, bolts, nuts, screens) will be assessed for priority and repaired as soon as possible or as required depending on the nature of the defect (See Appendix E for an example of the STI SP001 Standard Monthly Inspection Checklist). Annually - Annual External Inspection (Identified as P in Table 8-2): A more detailed examination of the tank and appurtenances shall be performed on an annual basis (See Appendix E for an example of the STI SP001 Standard Annual Inspection Checklist). | No Mission Impact
| 40C35 | LE404 | Bulk Storage | Aboveground Piping | Piping |  | N/A | N/A | N/A |  |  | X | 6-1.3 | No Manufacturer Requirements Available | Weekly - Conduct petroleum fuel piping visual inspection in accordance with Section 6-1.5 Pipeline Visual Inspection. | No Mission impact
| 40C35 | LE404 | Bulk Storage | Emergency Vents | Vent |  | Morrison Brothers | 244O | Unknown |  |  | X | 8-9.4 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE404 | Bulk Storage | Flame Arrestors | Vent |  | Morrison Brothers | 351S & 748A | N/A |  |  | X | 8-9.5 | No Manufacturer Requirements Available | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE404 | Bulk Storage | Pressure Relief Valves | Pressure Relief Valves |  | Taylor | 82E5351511 | 1" |  | X |  | 4-3.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS
| 40C35 | LE405 | Bulk Storage | Product Saver | Product Saver |  | N/A | N/A | 55 gals | X |  |  | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Sliding Vane Pump | Rotary Vane Pump |  | Blackmere | XMLF1125B | 1/4" | X |  | X | 3-8.2.1 | Check for unusual noise, vibration, temperature and leaks. Change Oil Annually | No Operator Requirement | No Mission Impact
| 40C36 | LE401 | Bulk Storage | Electric Motor | Product Saver |  | Baldoi | B55811917 | N/A | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE405 | Bulk Storage | Sliding Vane Pump | Rotary Vane Pump |  | MP Pumps | 50133 | 1" | X |  | X | 3-8.2.1 | Check for unusual noise, vibration, temperature and leaks. Change Oil Annually | No Operator Requirement | No Mission Impact
| 40C36 | LE401 | Bulk Storage | Electric Motor | Product Saver |  | Leeson | ACC34XL5B | N/A | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Temporary Mission Impact
| 40C35 | LE405 | Bulk Storage | Above Ground Piping and Equipment Coatings | Piping |  | N/A | N/A | N/A | X |  |  | 6-10.1 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Above Ground Piping and Equipment Coatings | Return To Bulk |  | N/A | N/A | 3" | X |  |  | 6-10.1 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Ball Valve | Ball Valve |  | Valworx | 553024 | 3" | X |  |  | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Fill Ports | Fill Ports |  | N/A | N/A | N/A | X |  | X | 8-9.12 | Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. | Daily - Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. Ensure the spill bucket is clean of dirt, trash, water, and fuel. | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Fill Ports | Fill Ports |  | N/A | N/A | N/A | X |  | X | 8-9.12 | Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. | Daily - Ensure fill port covers are installed and are not damaged or broken. Ensure fill port covers are identified by fuel type and are installed on the correct tank. Visually inspect the fill port spill bucket to ensure there are no cracks, budges, or holes. Ensure the spill bucket is clean of dirt, trash, water, and fuel. | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Back Pressure Control Valves | Control Valve |  | Cla Val | M119 | 300 psi | X | X |  | 4-4.2.6 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | No Mission Impact
| 40C35 | LE405 | Bulk Storage | Positive Displacement Meter | Return-to-Bulk |  | Liquid Controls | M-10-2 | 15 - 150 gpm |  | X |  | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS
| 40C35 | LE405 | Bulk Storage | Security Fencing | Security Fencing |  | N/A | N/A | N/A | X |  | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 40C35 | LE408 | Bulk Storage | Exterior Lighting | Exterior Lighting |  | N/A | N/A | N/A | X |  | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE418 | Bulk Storage | Exterior Lighting | Exterior Lighting |  | N/A | N/A | N/A | X |  | X | 9-1.8 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C35 | LE406 | Bulk Storage | Chain Link Entrance Gate to Fuel Farm, AASF | Chain Link Entrance Gate to Fuel Farm, AASF |  | N/A | N/A | N/A | X |  | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 40C35 | LE407 | Bulk Storage | Chain Link Pedestrian Gate @ Fuel Farm, AASF | Chain Link Pedestrian Gate @ Fuel Farm, AASF |  | N/A | N/A | N/A | X |  | X | 11-1.1 | No Manufacturer Requirements Available | Monthly - Remove debris from around security fence. Inspect fence grounding points. Ensure connections are not loose or damage. | No Mission Impact
| 40C35 | OILSP | Bulk Storage | GRAVITY OIL AND GREASE SEPARATOR | GRAVITY OIL AND GREASE SEPARATOR |  | N/A | N/A | N/A | X |  | X | 11-5 | No Manufacturer Requirements Available | No Operator Requirement | No Mission Impact
| 40C36 | OILSP | Bulk Storage | Eye Wash Station (Portable Bottles) | Eye Wash Station (Portable Bottles) |  | Eye Saline | N/A | 946 Mil | X | X | X | 11-3
| 40C35 | LE411 |  | Green Transformer, for Fuel Farm, AASF |  |  | N/A | N/A | N/A
| 40C35 | LE412 |  | Concrete Pad East, for Storm Sewer Drainage, Fuel Farm |  |  | N/A | N/A | N/A
| 40C35 | LE413 |  | Concrete Pad West, for Storm Sewer Drainage, Fuel Farm |  |  | N/A | N/A | N/A
| 40C35 | LE414 |  | Asphalt Cantonment Road to Fuel Farm, AASF |  |  | N/A | N/A | N/A
| 40C35 | LE415 |  | Storm Sewer for Fuel Farm, AASF |  |  | N/A | N/A | N/A
| 40C35 | LE417 |  | Plant Utility Building @ Fuel Farm |  |  | N/A | N/A | N/A
| 40C35 | LE419 |  | Asphalt Cantonment Road for Fuel Truck Parking |  |  | N/A | N/A | N/A
| 40C35 | LE420 |  | Industrial Waste Sewer for Fuel Truck Parking Area |  |  | N/A | N/A | N/A
| 40C35 | LE421 |  | Industrial Waste Sewer for Fuel Farm |  |  | N/A | N/A | N/A
| 40C35 | FTKOA |  | AIRCRAFT FUEL TRUCK LOADING FACILITY |  |  | N/A | N/A | N/A
| 40C35 | FTKOD |  | AIRCRAFT FUEL TRUCK LOADING FACILITY |  |  | N/A | N/A | N/A
| 40C35 | LE400 |  | AIRCRAFT FUEL TRUCK LOADING FACILITY |  |  | N/A | N/A | N/A
| 40C35 | FTKOM |  | AIRCRAFT FUEL TRUCK LOADING FACILITY |  |  | N/A | N/A | N/A
Instructions:
1. Input all data as indicated on the sheet.
2. Additional documents referred to in the Special Considerations column shall be included as an appendix to this FMP.
3. The contractor shall generate a Component Unique Identifier (CUID) for each component utilizing the Component Acronym Sheet within this Work Book. The unique identifier must use the following:
Three letter Site Code - Facility # - Component Acronym - Sequential number
Example: AAD-00063A-RCVL-0001
If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment. Base Asset ID if used by site shall be cross referenced with CUID appropriately.
4. Utilize the UFC Section Reference Work Category as noted on the Component Acronym Sheet.
5. Enter any applicable manufacturer requirements not stated in the UFC. References are acceptable with attachments.
6. Enter any applicable operator support or government owned equipment required to complete the RM task.
7. Enter impact on system availability by performing the RM task. This could include shutdown, lockout, or similar impacts.
8. Enter contract information for any other contract, contractor, or government personnel performing the applicable task. This is applicable to other Centrally Managed Programs, SRM, MILCON, or Public Works/Civil Engineering projects.
9. Print Hard Copies as 11x17.

## FS-PF Schedule
FILTER SEPARATOR/PRE-FILTER MAINTENANCE SCHEDULES
Applicable Facility Assets | [10 empty] | Coalescer/Separator Information | [7 empty] | Special Considerations
Real Property Unique Identifier (RPUID) | Real Property Facility # | Real Property Facility Name | Operational Area | Component Type | Base Asset ID | Component Unique Identifier (CUID) | Make | Model | Capacity (GPM) | UFC Section Reference | Number of Coalescer Cartridges | Number of Separator Cartridges | Coalescer Cartridges Model # | Separator Cartridge Model # | Clean or Replace Separator Cartridge | Gasket Model # | Date Last Replaced | Replacement Due Date | Operator/Equipment Requirements | System Availability | Site Self Performs (Y/N) | Comments
| 40C35 | FTKOA | Bulk Storage | Filter Separators | Issue Filter Separator 1 |  | Velcon | HV2838200 | 600 GPM | 3-6.2 | 7 | 2 | NSN 4330-01-451-3134 | 4330-01-491-4712 | Replace | G-0769 |  | 2025-05-24 |  |  | N | RMMR Contractor to Perform
| 40C35 | FTKOD | Bulk Storage | Filter Separators | Issue Filter Separator 2 |  | Velcon | HV2838200 | 600 GPM | 3-6.2 | 7 | 2 | NSN 4330-01-451-3134 | 4330-01-491-4712 | Replace | G-0769 |  | 2025-05-24 |  |  | N | RMMR Contractor to Perform
| 40C35 | FTKOM | Bulk Storage | Filter Separators | Receipt Filter Separator 1 |  | Velcon | HV2838200 | 600 GPM | 3-6.2 | 7 | 2 | NSN 4330-01-451-3134 | 4330-01-491-4712 | Replace | G-0769 |  | 2025-05-24 |  |  | N | RMMR Contractor to Perform
| 40C35 | LE400 | Bulk Storage | Filter Separators | Receipt Filter Separator 2 |  | Velcon | HV2838200 | 600 GPM | 3-6.2 | 7 | 2 | NSN 4330-01-451-3134 | 4330-01-491-4712 | Replace | G-0769 |  | 2025-05-24 |  |  | N | RMMR Contractor to Perform
Instructions:
1. Input all data as indicated on the sheet.
2. Additional documents referred to in the Special Considerations column shall be included as an appendix to this FMP.
3. The contractor shall generate a Component Unique Identifier (CUID) for each component utilizing the Component Acronym Sheet within this Work Book. The unique identifier must use the following:
Three letter Site Code - Facility # - Component Acronym - Sequential number
Example: AAD-00063A-RCVL-0001
If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment.
4. Utilize the UFC Section Reference Work Category as noted on the Component Acronym Sheet.
5. Enter any applicable manufacturer requirements not stated in the UFC. References are acceptable with attachments.
6. Enter any applicable operator support or government owned equipment required to complete the RM task.
7. Enter impact on system availability by performing the RM task. This could include shutdown, lockout, or similar impacts.
8. Filter Separators and Pre-Filters identified here shall also be provided in the Task Matrix Tab.
9. Print Hard Copies as 11x17.

## Component Acronym
Component Unique Identifier: | Site Code-Facility #-Component Acronym-Sequential #
Example: | AAD-00063A-RCVL-0001
NOTE: If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment
DLA Work Type Category | UFC Section Reference Work Category (Revised per Change 1, 29 April 2021) | Component Acronym
Air Compressors | Air Compressors | AIRC
Alarms | Externally Mounted Level Alarms (Section 8-9.9.1) | EMLA
| Internally Mounted Level Alarms (Section 8-9.9.3) | IMLA
Bollard | Bollards | BLRD
Building | Building HVAC | BHVAC
| Building Domestic Water System | BWTR
| Building Waste Water | BWSW
| Building - Lighting | BLTG
| Building - Architectural | BARCH
| Building - Fire Sprinkler System | BFIRE
Containment/Joints | Containment Systems (General) (Section 8-10.1) | CSGEN
| Concrete and Cement Brick Dike/Berm Walls (Section 8-10.2.1) | DKBW
| Dike/Berm Floors (Section 8-10.2.2) | DKBF
| Earthen Dike Walls (Section 8-10.3) | ETHDW
| Self-Diking or Vaulted Tank Containment (Section 8-10.4) | SDVTCS
| Flexible Membrane Liners (Section 8-10.5) | FXML
| Fuel Truck and Rail Car Containment Areas (Section 11-1.1) | FTKRCC
| Remote Spill Containment (Section 11-1.2) | RSCS
| Piers and Wharves Fuel Containment Systems (Section 5-1.2) - Testing | FPWCT
| Fuel Pier/Wharf Containment (PWS Section 3) | FPWC
Corrosion Control/Coatings | Aboveground Piping and Equipment Coatings (Section 6-10.1) | AGPCT
Miscellaneous | Miscellaneous Deactivated Components (Section 12-5) | MDEAC
Electrical/Lighting | Lighting (Section 9-1.8) | LIGHT
Electrical/Power | Electrical Equipment (Section 9-1.2) | ELEQ
| Power Cables (Section 9-1.3) | PWRCBL
| Motor Controls (Section 9-1.4) | MTRCT
| Panelboards (Section 9-1.5) | PNLB
| Electric Motors (Section 9-1.7) | ELEMT
| Electronic Equipment (9-1.9) | ELTREQ
| Card and Key Locks (Section 9-3) | CKLK
Electrical/Protection | Power Grounding Systems (Section 9-1.6.1) | PWRGS
| Static Grounding Systems (Section 9-1.6.2) | STGS
| Cathodic Protection (Section 9-2.1) | CP
| Lightning Surge Arresters (Section 9-2.2.1) | LSAR
| Lightning Protection Systems (Section 9-4) | LPTS
| Ground Verification System (Section 9-5) | GRVS
| Electronic Overfill Protection Systems (Section 9-6) | EOPS
Eyewash/Shower | Emergency Eyewash/Showers (Section 11-3) | EMEWSH
Fencing/ Gates | Fencing | FENC
| Gates | GATE
Filtration | Pre-Filters (Section 3-6.1) | PFVSL
| Filter Separators (Section 3-6.2) | FLSP
| Haypack Filters (Section 3-6.3) | HPKF
| Basket Strainers (Section 3-6.4) | BSTR
| Filter Separator Sump Heaters (Section 3-6.5) | FSSH
| Sidestream Filtration Systems (Section 8-9.11) | SSFTS
Fire Suppression Equipment | Flame Arrestors (Section 8-9.5) | FLMARR
| Foam Fire Protection Systems (Section 8-9.15) | FFPS
| Fire Protection Systems - Wet Pipe | FPRS
Fuel Laboratories | Ventilation Hoods (Section 11-4.1) | VENTHD
Gauges | Pressure and Pressure/Vacuum Gauges (Section 6-7.1) | PVGA
| Differential Pressure Gauges (Section 6-7.2) | DPGA
| Mechanical Tape Gauges (Section 8-9.7) | MTGA
| Mechanically Operated Tape Gauge (Section 8-9.8.1) | MOTGA
| Magnetostrictive Probes (Section 8-9.8.2) | MRPRB
| Servo Gauge (Section 8-9.8.3) | SRVGA
Generators | Back-Up Power Generators | BGEN
Heating Coils | Steam Type Heating Coils (Section 8-9.16.1) | STHC
| Thermal Fluid Type Heating Coils (Section 8-9.16.2) | TFTHC
| Electric Rod Type Heating (Section 8-9.16.3) | ERTH
Hoses | Loading Fuel Hoses (Section 3-9.1) | LDHS
| Offloading Fuel Hoses (Section 3-9.2) | OLHS
| Aircraft Fueling Hoses (Section 4-7.5) | ACFHS
Hydrazine | Hydrazine Charging Units (Section 10-3) | HDZCU
Inspections | Trouble Shoot | TRBST
| API 510 Inspections | API510
| API 653 or STI Inspection | API653
| Coatings Condition Survey | CCS
Issue/Receive - Ground | Dispenser Nozzles (Section 7-2) | DSNZ
| Dispenser Hoses (Section 7-3) | DSHS
| Breakaways (Section 7-4) | DSBW
| Swivels (Section 7-5) | DSSW
| Hose Retriever (Section 7-6) | HSRTV
| Dispenser Cabinet (Section 7-7) | DSCB
| Dispenser Meters (Section 7-8) | DSMTR
| Dispenser Filters (Section 7-9) | DSFLR
| Dispenser Strainers (Section 7-10) | DSSTR
| Ground Vehicle Fuel Piping (Section 7-11) | GVFP
| Emergency Shutoff Valves (Shear Valves) (Section 7-12) | ESHVL
| Dispenser Sumps (Section 7-13) | DSSMP
| Transition Sumps (Section 7-14) | TRSMP
| Remote Dispenser Pumps (Section 7-15.1) | RDSP
| Self-Contained Dispenser Pumps (Section 7-15.2) | SCDSP
| EFSO Systems (Section 7-16) | EFSO
| Stage I Vapor Recovery (Section 7-17.1) | SIVP
| Stage II Vapor Recovery (Section 7-17.2) | SIIVP
| Vapor Burners (Section 7-17.3) | VPBNR
| Point Sensor - Dry (Section 7-19.1.1) | PSDRY
| Automatic Line Leak Detector (Section 7-19.1.2) | ALLD
| Visual Monitoring (Section 7-20.1) | VSLM
Issue/Receive - Marine | Marine Receipt (Section 5-2) | MRNRCP
| Marine Issue (Section 5-3) | MRNISU
| Marine Loading Arms (Section 5-4) | MRNLA
| Marine Transfer Hoses (Section 5-5.1) | MBTHS
| Underwater Hoses (Section 5-5.2) | UWHS
| Single Point Mooring Systems (Section 5-7.1) | SPMSS
| Multi Point Mooring Systems (Section 5-7.2) | MPMSS
| Submerged Piping Systems (Section 5-8) | SMPS
| Boom Reels (Section 5-9) | BMRL
Liquefied Petroleum | Liquefied Petroleum Tanks (Section 10-1.1) | LPTANK
| Liquefied Petroleum Pipelines (Section 10-1.2) | LPPIPE
| Liquefied Petroleum Vapor Lines (Section 10-1.3) | LPVPL
| LPG Vaporizers (Section 10-1.4) | LPGVPZ
| Petroleum Gas Regulators (Section 10-1.5) | PGREG
| Liquefied Petroleum Gas Hoses (Section 10-1.6) | LPGHS
Meter/ calibrations | Positive Displacement Meters (Section 3-7.1) | PDMT
| Turbine Flow Meters (Section 3-7.2) | TBFMT
| Orifice Flow Meters (Section 3-7.3) | OFMT
Natural Disaster | Natural Disaster
Natural Gas | CNG Piping (Section 10-2.1) | NGPIPE
| CNG Compressors (Section 10-2.2) | NGCOMP
| CNG Storage (Section 10-2.3) | NGSTOR
| CNG Dispensers (Section 10-2.4) | NGDS
| CNG Dispenser Hoses (Section 10-2.5) | NGDSHS
Nozzle | Hydrant Adapters (Section 4-7.2) | HADP
| Fueling Nozzles (Section 4-7.3) | FLNZ
Other | Fuel Additive Injectors (Section 3-11) | FAIJ
Pantograph | Fixed Pantographs (Section 4-7.1.1) | FXPNT
| Detachable Pantographs (Section 4-7.1.2) | DTPNT
Piping | On-Base Pipelines (Section 6-1.1) | OBPL
| Non-DOT Regulated (Section 6-1.2.1) | NDPL
| Aboveground Piping (Section 6-1.3) | AGPL
| Double-Wall Piping (Section 6-1.4) | DWPL
| Low Point Drains (Section 6-12.1) | LPDN
| High Point Vents (Section 6-12.2) | HPVT
| Sight Flow Indicators (Section 6-12.3) | SFND
| Rope Sensor Systems (Section 6-13.1.1) | RPSS
| Point Sensor - Dry (Section 6-13.1.2) | PSDRY
| Visual Monitoring (Section 6-14.1) | VSLM
| Pipe Penetrations (Section 8-10.6) | PPEN
| Deactivated Petroleum Fuel Pipelines (Section 12-3) | DEACPL
Pressure/Temperature Control | Air Eliminator Tanks (Section 3-10.1) | AELT
| Automatic Air Vents (Section 3-10.2) | AAVT
| Surge Suppressors (Section 4-7.4) | SRGSP
| Thermal and Pressure Relief Valves (Section 6-6.3) | TPRVL
| Pressure Transmitters (Section 6-7.3) | PRTR
| Differential Pressure Transmitters (Section 6-7.4) | DPTR
| Flexible Ball Joints (Section 6-8) | FBLJT
| Dial Thermometer (Section 6-9.1) | DTHMR
| Emergency Vents (Section 8-9.4) | EMGVT
Pump | Centrifugal Pumps (Section 3-8.1) | CENP
| Vertical Inline Pumps (Section 3-8.2) | VILP
| Vertical Turbine/Submerged Turbine Pumps (Section 3-8.3) | VTSP
| Sliding Vane Pumps (Section 3-8.5) | SLVP
| Gear Pumps (Section 3-8.6) | GERP
| Diaphragm Pumps (Section 3-8.7) | DIAP
| Internal Combustion Drives (Section 3-8.8) | ICDR
| Gearboxes (Section 3-8.9) | GRBX
| Deactivated Petroleum Fuel Pumps (Section 12-4) | DEACP
Signage/Markings | Signage and Markings (Section 2-7) | SIGN
Structures | Pumphouse/Filter Buildings (Section 11-2.1) | PFBLDG
| Canopies (Section 11-2.2) | CNPY
| Cranes and Hoists (Section 11-6) | CRNHST
Tank | Aboveground Field-Erected Tanks (Section 8-4) | AGFET
| Geodesic Dome Roofs (Section 8-4.2) | GEODR
| Foundations (Section 8-4.3) | FOUND
| Aboveground Shop Fabricated Tanks (Section 8-5.1) | AGSFP
| Self-Diking or Vaulted Tanks (Section 8-5.2) | SDVT
| Rectangular Concrete-Encased Tanks (Section 8-5.3) | RCET
| Single-Walled Underground Shop-Fabricated Tanks (Section 8-5.4.1) | UGSSFT
| Double-Walled Underground Shop-Fabricated Tanks (Section 8-5.4.2) | UGDSFT
| Underground Field-Constructed Tanks (Cut and Cover Tanks) (Section 8-6) | UGFET
| Tank Cleaning (Section 8-7) | TCLEAN
| Aluminum Honeycomb Floating Pans (Section 8-9.1.1) | AHFP
| Steel Floating Pans (Section 8-9.1.2) | STLFP
| Pontoon Floating Pans (Section 8-9.1.3) | PTNFP
| Floating Roofs (Section 8-9.1.4) | FLTRF
| Floating Roof and Pan Pressure/Vacuum Vents (Section 8-9.1.5) | FPPVV
| Floating Roof and Pan Legs (Section 8-9.1.6) | FRPLG
| Secondary Tank Bottoms (Section 8-9.2) | SNDTB
| Tank Pressure/Vacuum Vents (Section 8-9.3) | TPVVT
| Product Saver Tanks (Section 8-9.10) | PRDST
| Fill Ports (Section 8-9.12) | FPRT
| Point Sensor - Dry (Section 8-9.13.1) | PSDRY
| Point Sensor - Wet (Section 8-9.13.2) | PSWET
| Point Sensor - Pressure/Vacuum (Section 8-9.13.3) | PSPV
| Visual Leak Detection (Section 8-9.13.4) | VSLLD
| Floating Suction Lines (Section 8-9.14) | FLTSL
| Stilling Wells (Section 8-9.17) | STGW
| Deactivated Petroleum Fuel Tanks (Section 12-2) | DEACT
Testing | Pressure Testing
Underground Pits | Isolation Valve Pits (Section 6-11.1) | ISVLP
| Hydrant Fuel Pits (Section 6-11.2) | HDFP
| High Point Vent Pits (Section 6-11.3) | HPVP
| Low Point Drain Pits (Section 6-11.4) | LPDP
| Lateral Control Pits (Section 6-11.5) | LTCP
Valves | General System Control Valves (Section 4-3.2.1) | GSCVL
| Refuel Control Valves (Section 4-3.2.5) | RCVL
| Pressure Relief Valves (Section 4-3.2.6) | PRCVL
| Defuel Control Valve (Section 4-3.2.7) | DFCVL
| Dual Rate-of-Flow Control Valves (Section 4-3.2.8) | DRFCVL
| Combination Dual Rate-of-Flow Control and Solenoid Valves (Section 4-3.3.1) | CFSCVL
| Dual Pressure Relief, Solenoid Shutoff, and Check Valves (Section 4-3.3.2) | DPSCVL
| Non-Surge Check Valves (Section 4-4.2.1) | NSCKVL
| Filter Separator Control Valves (Section 4-4.2.2) | FSCVL
| Defuel/Flush Valves (Section 4-4.2.3) | DFFCVL
| Issue Venturi (Section 4-4.2.4) | ISVTR
| Return Venturi (Section 4-4.2.5) | RTVTR
| Back Pressure Control Valves (Section 4-4.2.6) | BPCVL
| Pressure Control Valves (Section 4-4.2.7) | PCVL
| Hydrant Control Valves (Section 4-4.2.8) | HCVL
| Emergency Shut-off Valves (Section 4-4.2.9) | ESOVL
| Pantograph Control Valves (Section 4-5.2.12) | PTCVL
| Pantograph Pressure Control Valves (Section 4-5.2.13) | PTPCVL
| Overfill Valve for Product Recovery Tanks (Section 4-8.1) | OVLPRT
| Plug Valves - Lubricated (Section 6-6.2.1) | PLVL
| Plug Valves - Non-lubricated (Section 6-6.2.2) | NPLVL
| Gate Valves (Section 6-6.2.3) | GTVL
| Ball Valves (Section 6-6.2.4) | BLVL
| Double Block and Bleed Valves (Section 6-6.2.5) | DBBVL
| Butterfly Valves (Section 6-6.2.6) | BFVL
| Globe Valves (Section 6-6.2.7) | GLVL
| Check Valves (Section 6-6.2.8) | CKVL
| Line Blanks, Ring Spacers, and Spectacle Blinds (Section 6-6.2.9) | BLIND
| Manual Valve Gear Operators (Section 6-6.2.10) | MVLGO
| Fire Valves (Section 6-6.4.1) | FRVL
| Fusible Link Butterfly Valves (Section 6-6.4.2) | FLBFVL
| Truck Fill Valves (Section 6-6.5.1) | TFVL
| Motor Operators (Section 6-6.6) | MTROP
| External High Level Shutoff Valves (HLSO) (Section 8-9.6.1) | EHLSVL
| Internal HLSO Valves (Section 8-9.6.2) | IHLSVL
Waste | Oil/Water Separators (Section 11-5) | OWS

## Versions and Notes
Version | Date | Description of changes
v2.0 | 2021-08-18 | Updated Task Matrix to meet UFC 3-460-03 Change 1 , 29 April 2021
Updated Component Acronym Tab to meet UFC 3-460-03 Change 1 , 29 April 2021
v2.1 | 2022-04-20 | Task Matrix Tab - Deleted all services facility # columns and combined into one. Renamed "Real Property Facility #"
Task Matrix Tab - Added "RPUID" to Real Property Unique Identifier column
Task Matrix Tab - Added "Real Property" to Facility Name
Task Matrix Tab - Added column for "Base Asset ID"
Task Matrix Tab - Added "Additional" and "RM" to Manufacturer Requirements
Task Matrix Tab - Changed Comment note for Filter Separator
Task Matrix Tab - Changed Note #3 To add "Base Asset ID if used by site shall be cross referenced with CUID appropriately."
Task Matrix Tab - Changed note #7 under instructions for Task Matrix to clarify this column
Task Matrix Tab - Changed note #8 under instructions for Task Matrix to clarify this column
Added new tab for RM schedule to be included
Added new Tab for Filter Separator/Pre-Filter Schedule with instructions
Administrative Tab - changed Installation to Site and added Site Code to comply with new requirements as the three letter DLA site code is obsolete
General Facility Description - Changed the Instructions
Reversed columns 'Base Asset ID' and 'CUID' to match RM report for all tabs
Added FMP version to footer
v2.2 | 2022-10-31 | Administrative Tab - Added rows for POC Name for all
Administrative Tab - Added RPSUID in cell B2
General Facility Description Tab - Added "fuel type"
Communication Plan Tab - added "coordination for access"
Safety Tab - Changed instructions to read "Site Specific Addendum and Activity Hazard Analysis, which are Attachments to the APP, specific to activities or tasks related to recurring maintenance for this site."
Changed footer for tabs to FMP v2.2
Task Matrix and FS/PF Schedule added not to print as 11x17. Also changed in page layout.