## Administrative
Location | Site Name | Vance AFB Site #1
| RPSUID | 3375
| DLA Site Code | VNC
| Hours of Operation | 24 Hours of Operation
| Address | 1523 West Southgate Road, Enid, OK 73705
Contract | Contractor
Contract #
Local POCs | QAE Name
QAE Phone
QAE Email
Alt QAE Name
Alt QAE Phone
Alt QAE Email
DLA/SCP POCs | DLA PM Name
DLA PM Phone
DLA PM Email
SCP PM Name
SCP PM Phone
SCP PM Email
Contractor POCs | Contractor PM Name
Contractor PM Phone
Contractor PM Email
Contractor QC Name
Contractor QC Phone
Contractor QC Email
Contractor SM Name
Contractor SM Phone
Contractor SM Email
USACE POCs | USACE PM/COR Name
USACE PM/COR Phone
USACE PM/COR Email
USACE PE Name
USACE PE Phone
USACE PE Email
USACE KO Name
USACE KO Phone
USACE KO Email
Instructions:
This table shows the minimum information required. Additional details should be included based on site specific requirements. Additional POCs may be required.

## General Facility Description
Facility Description
Purpose: This Facility Maintenance Plan provides guidance for Contractor personnel in the operation, inspection, and maintenance of permanently installed fuel facilities operated under the control of the Quality Assurance Evaluators. Federal, state, and local environmental laws and regulations shall be complied with if this plan is in conflict with them. Scope: The instructions prescribed by this plan outline general fuels maintenance information associated with fuel storage and dispensing systems and provides the minimum periodic contractor maintenance and inspection criteria requirements for the systems. This plan is to be used in conjunction with other existing directives governing fuel system operations and maintenance requirements. Conotractor will properly maintain and repair federally funded petroleum systems and facilities in order to provide compliance with applicable code, criteria, and federal, state, local and/or host nation regulations. Fuels Facilities: Organizational tanks, and associated dispensing equipment are maintained and operated by the owning organization. Fuel system maintenance contractors shall perform all maintenance and associated procurement actions on installed fuel systems. Each installation under the Southwest Division contract are military land-based facilities who receive, store, distribute, and/or dispense liquid fuels. Standard fuel system equipment includes: a) Above Ground Sorage Stanks (AST), Underground Storage Tanks (UST) b) Filter/separator and other filtration device maintenance access, particularly element removal. c) Manual valves d) Meter Registers, and Flow Meters. e) Control Valves. f) Pumps g) Tank Monitoring Equipment and Instruments h) Alarms i) Fire Fighting Equipment Site Specific General Information:
Instructions:
Include a general facility overview and description of each fuel system for the sites in accordance with UFC 3-460-01. Examples include: Bulk Storage Facilities, Aircraft Fueling Facilities, Marine and Dispensing Facilities, Ground Products Fueling Facilities, Alternate POL Facilities, and Support Facilities. Also include facility #s, facility names, fuel type, photos, and any other pertinent information.
Include Site Specific Conditions and Restrictions in this tab.

## Communication Plan
Instructions:
Communication plan shall address in/out briefs, lines of communication, coordination for access, etc.

## Safety
Instructions:
Site Specific Addendum and Activity Hazard Analysis, which are Attachments to the APP, specific to activities or tasks related to recurring maintenance for this site.

## RM Schedule
Instructions:
Link RM schedule here

## Task Matrix
Applicable Facility Assets | [9 empty] | UFC System Level Maintenance Frequency |  |  |  | Special Considerations
Real Property Unique Identifier (RPUID) | Real Property Facility # | Real Property Facility Name | Operational Area | Component Type | Base Asset ID | Component Unique Identifier (CUID) | Make | Model | Capacity/Size | Q | S | A | UFC Section Reference | Additional Manufacturer RM Requirements | Operator/ equipment Requirements | System availability | Other Contract | Comments
| 109 | Fill stands | 109 Fillstands | Canopies | Fillstand 1 canopy |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Canopy-F/S #1
| 109 | Fill stands | 109 Fillstands | Canopies | Fillstand 2 canopy |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Canopy-F/S#2
| 109 | Fill stands | 109 Fillstands | Canopies | Fillstand 3 canopy |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Canopy-F/S #3
| 109 | Fill stands | 109 Fillstands | Emergency Eyewash/Showers | Emergency Eyewash-Fac 309 |  | Haws | Unmarked | 2.0 In. | X | X | X | 11-3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Emergency Eyewash-Fac 309
| 109 | Fill stands | 109 Fillstands | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 109 | Fill stands | 109 Fillstands | Air Eliminator Tanks | F/S 1 air eliminator |  | Armstrong | A11AV | 1.0 In. | X | X | X | 3-10.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | F/S 1 air eliminator
| 109 | Fill stands | 109 Fillstands | Air Eliminator Tanks | F/S 3 air eliminator |  | Armstrong | A11AV | 1.0 In. | X | X | X | 3-10.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Filter Separators | F/S 1 |  | Facet | HCS-643-236 | 600 GPM GPM/SCFM Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS |  | F/S 1
| 109 | Fill stands | 109 Fillstands | Filter Separators | F/S 3 |  | Facet | HCS-643-236 | 600 GPM GPM/SCFM Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS |  | Filter Separator #3
| 109 | Fill stands | 109 Fillstands | Filter Separators | F/S 2 |  | Facet | HCS-643-236 | 600 GPM GPM/SCFM Gallons | X | X | 0 | 3-6.2 | Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. Replace filter cartridges when the acceptable maximum differential pressure is reached, the maximum in-service duration has passed, or the fuel becomes visibly dirty or discolored. | Daily - Open drain under flow conditions until clear fuel is observed from the drain valve. Monitor differential pressure of coalescer cartridges. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Positive Displacement Meters | Fillstand 2 meter register |  | Veeder-Root | 788700063 | 600 GPM GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Positive Displacement Meters | Fillstand 3 meter register |  | Veeder-Root | 788700063 | 0-600 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS |  | fillstand 3 meter register
| 109 | Fill stands | 109 Fillstands | Positive Displacement Meters | Fillstand 1 meter register |  | Veeder-Root | 788700063 | 0-600 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS |  | Fillstand 1 meter register
| 109 | Fill stands | 109 Fillstands | Positive Displacement Meters | Fillstand 1 meter |  | LC | M-60-2 | 30-600 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS |  | Fillstand 1 meter
| 109 | Fill stands | 109 Fillstands | Positive Displacement Meters | Fillstand 3 meter |  | LC | M-60-2 | 30-600 GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS |  | Meter-F/S#3
| 109 | Fill stands | 109 Fillstands | Positive Displacement Meters | Fillstand 2 meter |  | LC | M-60-2 | 600 GPM GPM/SCFM | 0 | 0 | 0 | 3-7.1 | Inspect counter head for unusual noises and smooth operation. Inspect temperature element operation of meters equipped with temperature compensation feature | Monthly - Inspect counter head for unusual noises and smooth operation. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Loading Fuel Hoses | Fillstand 3 hose |  | Goodyear | G-200-8852 | 3.0 in. | X | X | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 108 fs1
| 109 | Fill stands | 109 Fillstands | Loading Fuel Hoses | Fillstand 2 hose |  | Goodyear | G-200-8852 | 3.0 in. | X | X | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Loading Fuel Hoses | Fillstand 1 hose |  | Goodyear | G-200-8852 | 3.0 in. | X | X | X | 3-9.1 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | Fillstand 1 hose
| 109 | Fill stands | 109 Fillstands | General System Control Valves | F/S 2 flange float control |  | Cal-Val | Not Legible | N/A | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | 108 fs2
| 109 | Fill stands | 109 Fillstands | General System Control Valves | F/S 1 flange float control |  | Cal-Val | Not Legible | N/A | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | F/S 1 flange float control
| 109 | Fill stands | 109 Fillstands | General System Control Valves | F/S 2 discharge control valve |  | Cal-Val | PN16 | 3.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | General System Control Valves | General system control-F/S#3 Down stream of meter |  | Cal-Val | Not Legible | 3.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | General system control-F/S#3 Down stream of meter
| 109 | Fill stands | 109 Fillstands | General System Control Valves | Fillstand 1 control valve |  | Cal-Val | 100 AF | 3.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Fillstand 1 control valve
| 109 | Fill stands | 109 Fillstands | General System Control Valves | F/S 3 discharge control valve |  | Cal-Val | Not Legible | 6.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | General System Control Valves | F/S 3 flange float control |  | Cal-Val | Not Legible | N/A | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Float control-F/S #3
| 109 | Fill stands | 109 Fillstands | Thermal and/or Pressure Relief Valves | F/S 3 PRV |  | Taylor | 82E5751311-10-10-0 | 1.0 in. 0 - 0 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | F/S 3 PRV range 226-450 psi
| 109 | Fill stands | 109 Fillstands | Thermal and/or Pressure Relief Valves | F/S 1 discharge PRV |  | Taylor | 82E3751311-10-10-0 | 1.0 in. 0 - 0 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | F/S 1 discharge PRV range 51-100psi
| 109 | Fill stands | 109 Fillstands | Thermal and/or Pressure Relief Valves | F/S 3 discharge PRV |  | Taylor | 82E3751311-10-10-0 | 1.0 in. 0 - 0 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Thermal and/or Pressure Relief Valves | F/S 2 PRV |  | Taylor | 82E3751311-10-10-0 | 1.0 in. 0 - 0 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | 109 fs 2 range 226-450 set @ 275
| 109 | Fill stands | 109 Fillstands | Thermal and/or Pressure Relief Valves | F/S 2 discharge PRV |  | Taylor | 02E3751311-10-10-0 | 1.0 in. 0 - 0 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | 109 fs2 51-100 set 80
| 109 | Fill stands | 109 Fillstands | Thermal and/or Pressure Relief Valves | F/S 1 PRV |  | Taylor | 82E5751311-10-10-0 | 1.0 in. 0 - 0 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | 109 fs1 set 275. 226-450
| 109 | Fill stands | 109 Fillstands | Filter Separator Control Valves | Fil sep control valve |  | Cal-Val | 104-661 | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Filter Separator Control Valves | F/S 1 control valve |  | Cal-Val | 100 AF | 6.0 in. | X | X | 0 | 4-4.2.2 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | F/S 1 control valve
| 109 | Fill stands | 109 Fillstands | Fueling Nozzles | Fillstand 2 nozzle |  | Carter | 64349 | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Fueling Nozzles | Fillstand 3 nozzle |  | Carter | 64349 | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Fueling Nozzles | Fillstand 1 nozzle |  | Carter | 64349 | 3.0 In. | X | X | 0 | 4-7.4 | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Quarterly - Inspect the condition of the dust cap at the aircraft adapter end and ensure it is in good working order. Dust caps must be attached to nozzles when they are not is use. Test leak resistance of poppet valve against full pump pressure. Inspect storage racks for moisture or dirt accumulation. Remove nozzle for inspection of content impinged upon the mesh screen. Clean and dry screens before nozzles are returned to service. Tests nozzle interlocks. Check the operation of the manual valve crank assembly for smooth and positive motion on a special test stand. | Partial System OOS |  | Fillstand 1 fueling nozzle
| 109 | Fill stands | 109 Fillstands | Sight Flow Indicators | F/S 2 sight glass |  | N/A | N/A | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 108 fs2
| 109 | Fill stands | 109 Fillstands | Sight Flow Indicators | F/S 1 sight glass |  | N/A | N/A | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | F/S 1 sightglass
| 109 | Fill stands | 109 Fillstands | Sight Flow Indicators | F/S 3 sight glass |  | N/A | N/A | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | Sight glass-F/S #3
| 109 | Fill stands | 109 Fillstands | Visual Monitoring | Fillstand 1 fall protection system |  | Fall Protection Systems | AR40 | N/A | 0 | 0 | 0 | 6-14.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Fill stand 1 fall protection system
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball balve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs 2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 108 fs 2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 108 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 air bleed valve |  | Flow -Tek | RF-15 | 0.75 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 air bleed valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 air eliminator iso valve |  | Flow -Tek | RF-15 | 0.75 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 air eliminator iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 PRV iso valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 PRV iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 sump drain valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 sump drain valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 sump drain valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 sump drain valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 air eliminator iso valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 air eliminator iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF15 | 0.75 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 test port valve discharges
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 discharge PRV iso valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 discharge PRV iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 discharge PRV iso valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 discharge PRV iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | Fillstand 1 pressure gauge iso valve |  | Painted / Not Legible | Painted / Not Legible | 0.75 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Fillstand 1 pressure gauge iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball Valve-F/S#3 |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball Valve-F/S#3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball Valve-F/S #3 |  | Flow -Tek | RF-15 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball Valve-F/S #3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Test port ball valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Test port ball valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Test port ball valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Sample port ball valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Ball Valves | Sample port inlet ball valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 test port valve inlet |  | Gammon | GTP 1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 test port valve inlet
| 109 | Fill stands | 109 Fillstands | Ball Valves | F/S 1 discharge sample valve |  | Gammon | GTP 1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 discharge sample valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | Fillstand 1 iso valve |  | WKM | Painted / Not Legible | 3.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Fill stand 1 iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | WKM | Painted / Not Legible | 3.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve-to pressure gauge inlet side Of meter-F/S#3 |  | Painted / Not Legible | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball valve-to pressure gauge inlet side Of meter-F/S#3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Discharge sample port ball valve |  | Schultz | Unmarked | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Ball Valves | Ball valve |  | Flow -Tek | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | F/S 1 PRV iso valve
| 109 | Fill stands | 109 Fillstands | Ball Valves | V-56 Ball valve-F/S#3 Downstream of meter |  | Dyna Seal | 3F-B111 | 3.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | V-56 Ball valve-F/S#3 Downstream of meter
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | Fil sep outlet DBB valve |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | F/S 1 Double block and bleed |  | TruSeal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | F/S 1 inlet iso valve
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | F/S 1 double block and bleed |  | TruSeal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | F/S 1 discharge iso valve
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | Fillstand 1 double block and bleed |  | TruSeal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Full stand 1 inlet iso valve
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | V-55 Double block and bleed inlet side of meter |  | TruSeal | 1-306R | 3.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | V-55 Double block and bleed inlet side of meter
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Globe Valves | F/S 2 globe valve |  | Kenco | Not Marked | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Globe Valves | F/S 2 globe valve |  | Kenco | Not Marked | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Globe Valves | F/S 3 globe valve |  | Kenco | Not Marked | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | Globe valve-F/S#3
| 109 | Fill stands | 109 Fillstands | Globe Valves | F/S 3 globe valve |  | Kenco | Not Marked | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | Globe valve-F/S#3
| 109 | Fill stands | 109 Fillstands | Pressure and Pressure/Vacuum Gauges | F/S 2 dp psi gauge |  | Not Labeled | Not Labeled | 0.25 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Pressure and Pressure/Vacuum Gauges | Fillstand 2 psi gauge |  | Wika | 233.53 | 0.25 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Pressure and Pressure/Vacuum Gauges | F/S 1 dp psi gauge |  | PFT Alexander | 800-696-1331 | 0.25 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | F/S 1 pressure gauge range 0-300
| 109 | Fill stands | 109 Fillstands | Pressure and Pressure/Vacuum Gauges | Fillstand 1 psi gauge |  | Wika | 233.53 | 0.5 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | Fill stand 1 pressure gauge
| 109 | Fill stands | 109 Fillstands | Pressure and Pressure/Vacuum Gauges | Fillstand 3 psi gauge |  | Wika | 233.53 | 0.25 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 109 fs3 0-200
| 109 | Fill stands | 109 Fillstands | Pressure and Pressure/Vacuum Gauges | Pressure gauge-inlet to meter F/S#3 |  | Wika | 233.54 | 1.0 in. 0 - 0 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | Pressure gauge-inlet to meter F/S#3
| 109 | Fill stands | 109 Fillstands | Differential Pressure Gauges | F/S 2 DP gauge |  | Schultz | SC-5150-30 | 0 - 0 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Differential Pressure Gauges | F/S 3 DP gauge |  | Schultz | SC-5150-30 | 0 - 0 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | EFSO Systems | EFSO bldg 109 |  | Unmarked | Unmarked | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | EFSO-adjacent to Fac 109
| 109 | Fill stands | 109 Fillstands | EFSO Systems | Fillstand 2 e-stop button |  | Cooper Crouse Hines | DSD933 | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | EFSO Systems | Fillstand 3 e-stop button |  | Cooper Crouse Hines | DSD933 | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | EFSO Systems | Fillstand 3 EFSO switch |  | Cooper Crouse Hines | DSD933 | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | EFSO Systems | Fillstand 1 EFSO switch |  | Cooper Crouse Hines | DSD933 | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | Fillstand 1 EFSO switch on/off
| 109 | Fill stands | 109 Fillstands | EFSO Systems | Fillstand 1 e -stop button |  | Cooper Crouse Hines | DSD933 | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | Fillstand 1 EFSO button
| 109 | Fill stands | 109 Fillstands | EFSO Systems | EFSO rear of bldg 116 |  | Unmarked | Unmarked | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | EFSO rear of 116
| 109 | Fill stands | 109 Fillstands | Automatic Line Leak Detector | Veeder Root-product recovery tank F/S area |  | Veeder-Root | TLS-300C | N/A | 0 | 0 | X | 7-19.1.2 | No Manufacturer Requirements Available | Daily - Ensure the monitoring panel associated with the detector(s) is powered on and no alarms are present. | Partial System OOS |  | Veeder Root-product recovery tank F/S area
| 109 | Fill stands | 109 Fillstands | Swivels | Fillstand 1 hose swivel |  | OPW | 3950F00301-GL | 3.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | 109 Fillstand 2
| 109 | Fill stands | 109 Fillstands | Swivels | Fillstand 3 hose swivel |  | OPW | 3950F00301-GL | 3.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | Fillstand 3 Hose swivel
| 109 | Fill stands | 109 Fillstands | Swivels | Fillstand 2 hose swivel |  | OPW | 3950F00301-GL | 3.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | Fillstand 1 swivel joint
| 109 | Fill stands | 109 Fillstands | Containment Systems | Protective bollards-adjacent to Fac 109 |  | N/A | N/A | N/A | 0 | 0 | 0 | 8-10.1 | No Manufacturer Requirements Available | Daily - Inspect containment systems for cleanliness, if accessible. | No Mission Impact |  | Protective bollards-adjacent to Fac 109
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | E stop switch |  | Cooper Crouse Hines | DSD933 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Explosion proof lighting-switch. Bldg 109 |  | Appleton Electric Co | Snap Switch | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Explosion proof lighting-switch. Bldg 109
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | 109 Audible alarm |  | Veeder-Root | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Audible alarm
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | 109 audible alarm acknowledge/reset |  | Veeder-Root | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 109 audible alarm acknowledge/reset
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Power Panel-Adjacent to Fac 109 |  | Square D | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Power Panel-Adjacent to Fac 109
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Electrical Box-adjacent to Fac 109 |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Box-adjacent to Fac 109
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Electrical Panel-Adjacent to Fac 109 |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel-Adjacent to Fac 109
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Electrical Panel-adjacent to Fac 109 |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel-adjacent to Fac 109
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Fillstand 2 deadman |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Fillstand 3 deadman |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Fac 109 bollards-45&3 bollards |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Fac 109 bollards-45
| 109 | Fill stands | 109 Fillstands | Electrical Equipment | Fillstand 1 deadman |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Fillstand 1 deadman switch
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 2 ground reel |  | Hannay Reels | HGR-50-50 | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 3 ground reel |  | Hannay Reels | HGR 50-50 | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs1
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 3 ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | F/S 2 ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | F/S 2 control valve ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | F/S 1 ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | F/S 1 ground
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 2 ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | F/S 1 ground rod |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | F/S 1 ground
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 1 ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Fillstand 1 ground
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 1 ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Fillstand 1 ground
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | F/S 3 ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | F/S 3 Ground
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | F/S 3 control valve ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 109 fs3
| 109 | Fill stands | 109 Fillstands | Static Grounding Systems | Fillstand 1 ground reel |  | Hannay Reels | HGR 50-50 | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Fillstand 1 ground reel
| 109 | Fill stands | 109 Fillstands | Lighting | Explosion proof lighting-Bldg 109 |  | Appleton Electric Co | A-51 Series | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Explosion proof lighting-Bldg 109
| 109 | Fill stands | 109 Fillstands | Lighting | F/S#2- Facility Lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | F/S#2- Facility Lighting
| 109 | Fill stands | 109 Fillstands | Lighting | Lighting-F/S#3 |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Lighting-F/S#3
| 109 | Fill stands | 109 Fillstands | Lighting | Facility Lighting-F/S#3 |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Facility Lighting-F/S#3
| 109 | Fill stands | 109 Fillstands | Lighting | Fs2 light |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 109 fs2
| 109 | Fill stands | 109 Fillstands | Cathodic Protection | Cathodic protection system |  | Dairyland | OVP2-3/1-37-100 (50/60Hz) | N/A | X | X | X | 9-2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Cathodic protection device 3ea. under CMP
| 109 | Fill stands | 109 Fillstands | Lightning Protection Systems | Lightning Protection System-F/S#1 |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Lightning Protection System-F/S#1
| 109 | Fill stands | 109 Fillstands | Lightning Protection Systems | Lightning Protection System-F/S#2 |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Lightning Protection Systems-F/S #2
| 109 | Fill stands | 109 Fillstands | Lightning Protection Systems | Lightning Protection Systems-F/S#3 |  | N/A | N/A | N/A | 0 | 0 | X | 9-4 | Proof Test : Confirm that the control module is indicating a dry condition (output relay closed). Bypass the safety function and take appropriate action to avoid a false trip Remove power from the WX system relay. Confirm that the relay opens within one (1) second. Reconnect power. Disconnect one of the wires to the sensor. Confirm that the relay opens within one (1) second. Reconnect power. Short the two sensor wires together. Confirm that the relay opens within one (1) second. Remove short. Remove the bypass and otherwise restore normal operation | No Operator Requirement | Partial System OOS |  | Lightning Protection Systems-F/S#3
| 109 | Fill stands | 109 Fillstands | Electronic Overfill Protection Systems | Fillstand 1 overfill protection |  | Scully | Intellitrol | N/A | X | X | 0 | 9-6 | Proof Test : Confirm that the control module is indicating a dry condition (output relay closed). Bypass the safety function and take appropriate action to avoid a false trip Remove power from the WX system relay. Confirm that the relay opens within one (1) second. Reconnect power. Disconnect one of the wires to the sensor. Confirm that the relay opens within one (1) second. Reconnect power. Short the two sensor wires together. Confirm that the relay opens within one (1) second. Remove short. Remove the bypass and otherwise restore normal operation | No Operator Requirement | Partial System OOS |  | Fillstand 1 scully system
| 109 | Fill stands | 109 Fillstands | Electronic Overfill Protection Systems | Fillstand 3 overfill protection |  | Scully | Intellitrol | N/A | X | X | 0 | 9-6 | Proof Test : Confirm that the control module is indicating a dry condition (output relay closed). Bypass the safety function and take appropriate action to avoid a false trip Remove power from the WX system relay. Confirm that the relay opens within one (1) second. Reconnect power. Disconnect one of the wires to the sensor. Confirm that the relay opens within one (1) second. Reconnect power. Short the two sensor wires together. Confirm that the relay opens within one (1) second. Remove short. Remove the bypass and otherwise restore normal operation | No Operator Requirement | Partial System OOS |  | 108 fs1
| 109 | Fill stands | 109 Fillstands | Electronic Overfill Protection Systems | Fillstand 2 overfill protection |  | Scully | Intellitrol | N/A | X | X | 0 | 9-6 | Proof Test : Confirm that the control module is indicating a dry condition (output relay closed). Bypass the safety function and take appropriate action to avoid a false trip Remove power from the WX system relay. Confirm that the relay opens within one (1) second. Reconnect power. Disconnect one of the wires to the sensor. Confirm that the relay opens within one (1) second. Reconnect power. Short the two sensor wires together. Confirm that the relay opens within one (1) second. Remove short. Remove the bypass and otherwise restore normal operation | No Operator Requirement | Partial System OOS |  | 109 fs2
| 112 | Fillstand product recovery tank | Fillstand product recovery | Underground Double-walled Shop-Fabricated Tanks | Fillstand product recovery tank |  | Unknown | Unknown | 600 Gallons | X | X | X | 8-5.4.2 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-4): Ensure all tank port covers are present, are in good condition, and seated firmly on the correct tank. Inspect tank stick gauge and ensure markings are legible and that the stick gauge is not warped or broken. Inspect tank for water using ATG or stick gauge with water-finding paste. Remove water found in tank. Open and inspect tank-top containment sumps and ensure no fuel or water is collected in the sumps. Check for and remove obstructions in tank fill pipe. | Partial System OOS |  | Fillstand product recovery tank
| 116 | Fuels Lab | 116 Fuels lab | Fuel Truck Containment Areas | Refueler parking yard |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | refueler parking yard
| 116 | Fuels Lab | 116 Fuels lab | Emergency Eyewash/Showers | Lab eyewash |  | Encon | Z358.1-1990 | 2.0 In. | X | X | X | 11-3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Counter mount eyewash
| 116 | Fuels Lab | 116 Fuels lab | Emergency Eyewash/Showers | Lab shower |  | Speakman | Unmarked | 2.0 In. | X | X | X | 11-3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 116 fuels lab
| 116 | Fuels Lab | 116 Fuels lab | Ventilation Hoods | Lab fume hood |  | Fisher Scientific | Allied | N/A | X | X | X | 11-4.1 | Daily visual inspection, check the fume hood for visible airflow blockage such as large items or containers near the slot opening. Other daily inspections include holding a tissue at the opening to observe inward airflow, maintaining clean surfaces inside the hood, and keeping the sash at an appropriate height when working and not working in the hood. | No Operator Requirement | No Mission Impact |  | Fuels Lab-Fume Hood
| 116 | Fuels Lab | 116 Fuels lab | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 116 | Fuels Lab | 116 Fuels lab | Isolation Valve Pits | Isolation Valve Pit |  | Not Legible | Not Legible | N/A | 0 | 0 | 0 | 6-11.1 | No Manufacturer Requirements Available | Monthly, or more often based on local conditions . Isolation valve pits should be inspected to ensure that the pits are dry and clean and that all components within the pit are clean and in good working order. Maintain seals and boot seals as appropriate. Obtain necessary confined space entry permits before entry. Inspect the pit for signs of fuel or water. Water or fuel should be removed from the pit as soon as possible and the source of water infiltration or fuel leak determined. Check for cracks in concrete and check piping penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no seepage of water into the pits. Make note of cracks in concrete and schedule maintenance as necessary. Check for fuel leaks at all flanged and other piping connections. Check for rusted or deteriorated ladders or grating platforms that might make entry unsafe. Check pit lids for proper sealing. Check rolling pit covers for ease of operation and signs of deterioration, damage or corrosion. Make sure required locks are in place and locking mechanisms are not broken. | Partial System OOS |  | Isolation Valve Pit
| 116 | Fuels Lab | 116 Fuels lab | Double Block and Bleed Valves | Transfer line DBB valve |  | Truseal | 1-306R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 116 valve iso pit
| 116 | Fuels Lab | 116 Fuels lab | Double Block and Bleed Valves | Transfer line DBB valve |  | TruSeal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Fillstand transfer line iso from pumphouse
| 116 | Fuels Lab | 116 Fuels lab | Electrical Equipment | Vent hood switches |  | Appleton Electric Co | EDSC150-F1 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Vent hood switches
| 116 | Fuels Lab | 116 Fuels lab | Lighting | Refueler parking yard-Lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Refueler parking yard-Lighting (4 poles-8 lights)
| 116 | Fuels Lab | 116 Fuels lab | Lighting | F/S#1 Lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | F/S#1 Lighting
| 264 | Pump House | 264 Pump house | Emergency Eyewash/Showers | Eyewash/shower |  | Haws | Unmarked | 2.0 In. | X | X | X | 11-3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 eyewash/shower
| 264 | Pump House | 264 Pump house | Oil/Water Separators | Oil water seperator |  | N/A | N/A | N/A | X | X | X | 11-5 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Oil water separator outside NE corner of tank 267
| 264 | Pump House | 264 Pump house | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 264 | Pump House | 264 Pump house | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly |  | No Mission Impact | Style D | 4.0 in. | X | X | 0 | 3-6.4 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly |  | No Mission Impact | Style D | 4.0 in. | X | X | 0 | 3-6.4 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Basket strainer-inlet to Pump#1
| 264 | Pump House | 264 Pump house | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly |  | No Mission Impact | Style D | 6.0 in. | X | X | 0 | 3-6.4 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump 2 inlet
| 264 | Pump House | 264 Pump house | Periodically checking for leaks. Timely cleaning or replacement of screen | Daily - Monitor and chart differential pressure measurements of basket strainers from readings taken during normal operations. Semi-annually if basket strainer is equipped with means to measure differential pressure; otherwise quarterly |  | No Mission Impact | Style D | 4.0 in. | X | X | 0 | 3-6.4 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Centrifugal Pumps | Pump 5 pump |  | Gorman-Rupp | RS3A31-BAR | 300 gpm GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Centrifugal Pumps | Pump 6 |  | Gorman Rupp | RS3A31-BAR | 300 gpm GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Centrifugal Pumps | Pump#1 |  | Gorman-Ruup | RS3A31-BAR | 300 gpm GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact |  | Pump 1
| 264 | Pump House | 264 Pump house | Centrifugal Pumps | Pump 2 |  | Gorman-Rupp | RS3A31-BAR | 300 gpm GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact |  | Pump 2
| 264 | Pump House | 264 Pump house | Offloading Fuel Hoses | Offload hose |  | Not Labled | Not Labled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 264 Offload hose
| 264 | Pump House | 264 Pump house | Offloading Fuel Hoses | Offload hose |  | Not Labled | Not Labled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 264 offload 3
| 264 | Pump House | 264 Pump house | Offloading Fuel Hoses | Offload hose |  | Not Labled | Not Labled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Offloading Fuel Hoses | Offload hose |  | Not Labled | Not Labled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Offloading Fuel Hoses | Offload hose |  | Not Labled | Not Labled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Offloading Fuel Hoses | Offload hose |  | Not Labled | Not Labled | 3.0 in. | X | X | X | 3-9.2 | Aircraft fueling hose shall be inspected before use each day. The hose shall be extended as it normally would be for fueling and checked for evidence of blistering, carcass saturation or separation, cuts, nicks, or abrasions that expose reinforcement material, and for slippage, misalignment, or leaks at couplings. | Weekly - Visually inspect hoses for loose covers, cracks, brittle surface coatings, exposed wire braids, exposed reinforcement, flattening, kinks, and bulges or soft spots which might indicate broken or displaced reinforcement. Monthly - Pressurize hose to normal working pressure. Check flanged and threaded connections for leaks and inspect hose couplers for fluid seepage by pushing at the base of the coupling with your thumbs; a hose softened by fluid seepage must be replaced. | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | General System Control Valves | Control discharge valve-pump#1 |  | Cal-Val | Not Legible | 6.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Control valve to outlet of Pump#1 V-72
| 264 | Pump House | 264 Pump house | General System Control Valves | Pump 2 control valve |  | Cal-Val | 100 AF | 6.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Pump 2 discharge control valve
| 264 | Pump House | 264 Pump house | Thermal and/or Pressure Relief Valves | Pressure relief valve |  | Taylor | 82E3751311-10-10-0 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | Pump manifold PRV
| 264 | Pump House | 264 Pump house | Thermal and/or Pressure Relief Valves | Prv |  | Taylor | 82E3751311-10-10-0 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Thermal and/or Pressure Relief Valves | Prv |  | Taylor | 82E3751311-10-10-0 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Sight Flow Indicators | Sight flow indicator |  | Visi-Flo | 1421DF | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 264 offload header 3
| 264 | Pump House | 264 Pump house | Sight Flow Indicators | Sight flow indicator |  | Visi-Flo | 1421DF | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 264 offload header 3
| 264 | Pump House | 264 Pump house | Sight Flow Indicators | Sight flow indicator |  | Visi-Flo | 1421DF | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Sight Flow Indicators | Sight flow indicator |  | Visi-Flo | 1421DF | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Sight Flow Indicators | Sight flow indicator |  | Visi-Flo | 1421DF | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Sight Flow Indicators | Sight flow indicator |  | Visi-Flo | 1421DF | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve |  | Mueller Co | A20806 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 264 drain valve
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve |  | Mueller Co | A20806 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 264 drain valve
| 264 | Pump House | 264 Pump house | Gate Valves | Pump air bleed valve |  | Painted / Not Legible | Painted / Not Legible | 0.5 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | Pump air bleed valve M-96
| 264 | Pump House | 264 Pump house | Gate Valves | Gate-valve M-84 |  | Painted / Not Legible | Painted / Not Legible | 0.75 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | Gate valve-M-84
| 264 | Pump House | 264 Pump house | Gate Valves | Pump air bleed valve |  | Painted / Not Legible | Painted / Not Legible | 0.5 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | Pump air bleed valve M-16
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve M-11 |  | Painted / Not Legible | Painted / Not Legible | 0.75 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | Gate Valve-M-11
| 264 | Pump House | 264 Pump house | Gate Valves | Pump 2 basket strainer drain |  | Painted / Not Legible | Painted / Not Legible | 0.5 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | Pump 2 inlet strainer drain
| 264 | Pump House | 264 Pump house | Gate Valves | PIV-adjacent to oil/water catchment basin |  | Mueller Co | A20806 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | PIV-adjacent to oil/water catchment basin
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve |  | Tufline | 6-150 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve |  | Tufline | 6-150 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve |  | Tufline | 6-150 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Gate Valves | Gate valve |  | Tufline | 6-150 | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Gate Valves | V-35 Gate Valve |  | OWG | Painted / Illegible | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | V-35 Gate Valve
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | 2000W0G | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | RF15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Ball Valves | Pump 2 discharge gauge iso valve |  | Flow -Tek | S20 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump discharge gauge iso valve
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve-inlet of pump#1 |  | Flow -Tek | 320 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball valve-inlet of pump#1
| 264 | Pump House | 264 Pump house | Ball Valves | Pump 2 gauge iso valve |  | Flow -Tek | S20 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump 2 inlet gauge iso valve
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | 2000W0G | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball valve-inlet to pump #1
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | RF15 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Ball Valves | Pressure Relief Isolation |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump inlet manifold PRV iso valve
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | RF15 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump inlet manifold PRV iso valve
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball valve-inlet the PR on outlet side of Pump#2
| 264 | Pump House | 264 Pump house | Ball Valves | Pump house Product recovery sump drain |  | Nibco | RF15 | 0.75 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump house product recovery sump drain valve
| 264 | Pump House | 264 Pump house | Ball Valves | Product recovery drain valve |  | Matco | 600WOC | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Product recovery drain valve
| 264 | Pump House | 264 Pump house | Ball Valves | Product recovery product drain valve |  | Matco | 600WOC | 1.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump house product recovery containment drain valve
| 264 | Pump House | 264 Pump house | Ball Valves | Pump 2 discharge sample port |  | Schultz | Accu-Sample | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump discharge sample port
| 264 | Pump House | 264 Pump house | Ball Valves | Sample Cock |  | Schultz | Accu-Sample | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Sample cock-inlet side of pump #1
| 264 | Pump House | 264 Pump house | Ball Valves | Pump 2 inlet sample port |  | Schultz | Accu-Sample | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Pump 2 inlet sample port
| 264 | Pump House | 264 Pump house | Ball Valves | Sampling Cock |  | Schultz | Accu-Sample | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Sample Cock-inlet of pump#1
| 264 | Pump House | 264 Pump house | Ball Valves | Fill stand low point |  | Force | Painted / Not Legible | 2.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low point fill stand line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Force | Painted / Not Legible | 4.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 offload header 3
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Force | Painted / Not Legible | 4.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | WKM | Painted / Not Legible | 4.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Painted / Not Legible | Painted / Not Legible | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 offload 3
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Painted / Not Legible | Painted / Not Legible | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Matco | 600WDG-150SWP | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Matco | Not Labeled | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Ball Valves | Ball valve |  | Nibco | 600 GWP | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-303R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Fill stand pipeline iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | TruSeal | 1-306 R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 265 pipeline iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | TruSeal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 267 pipeline iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | F832 | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | F633 | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | F329 | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Pump 2 inlet iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Pump manifold iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-308R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Pump manifold inlet iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | V-26 Double block and bleed inlet to Pump#1 |  | TruSeal | 01306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | V-26 Double block and bleed
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Pump 2 discharge iso valve
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | V-27 |  | TruSeal | F336 | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | V-27 Double block and bleed
| 264 | Pump House | 264 Pump house | Double Block and Bleed Valves | V-27 |  | TruSeal | F621 | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | V-21 Double block and bleed
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | Walworth | WCB | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 offload header check valve
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | Walworth | WCB 12946 | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 offload 3
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | Walworth | WCB | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | Walworth | WCB | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 offload 2
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | Walworth | WCB | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | Walworth | WCB | 4.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | P&C | 350 OW | 6.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Check Valves | Check valve |  | P&C | 227A4 | 6.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Pump 2 discharge pressure gauge |  | Trerice | 750LFSS4004LA070 | 0.5 in. -30 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | Pump 2 discharge pressure
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Pressure gauge-outlet of Pump#1 |  | Trerice | 750LFSS4004LA070 | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | Pressure gauge
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Pump 2 inlet gauge |  | Trerice | 750LFSS4004LA070 | 0.5 in. -30 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | Pump 2 inlet gauge
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Pressure gauge-inlet to Pump#1 |  | Trerice | 750LFSS4004LA070 | 0.5 in. 0 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | Pressure gauge-inlet to pump#1
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Psi/vacuum gauge |  | Trerice | 750LFSS4004LA070 | 0.5 in. -30 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Psi/vacuum gauge |  | Trerice | 750LFSS4004LA070 | 0.5 in. -30 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Psi/vacuum gauge |  | Trerice | 750LFSS4004LA070 | 0.5 in. -30 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Pressure and Pressure/Vacuum Gauges | Psi/vacuum gauge |  | Trerice | 750LFSS4004LA070 | 0.5 in. -30 - 300 PSI | X | X | X | 6-7.1 | Check operation of gauge. Ensure gauge is indicating pressure of the system. Inspect liquid level, and clean exterior glass. Calibrate as required dependent on use. | Monthly - Check operation of gauge. Ensure gauge is indicating pressure of the system. | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | EFSO Systems | E-stop switch |  | Cooper Crouse Hines | Unmarked | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | 264 offload 3
| 264 | Pump House | 264 Pump house | EFSO Systems | Emergency shut-off switch-offload#2 |  | Unmarked | Unmarked | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | Emergency Shut-off switch-offload#2
| 264 | Pump House | 264 Pump house | EFSO Systems | Emergency shut-off switch-offload #1 |  | Unmarked | Unmarked | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | Emergency shut-off switch-offload#1
| 264 | Pump House | 264 Pump house | Product Saver Tanks | Pump house PRT |  | Unmarked | Unmarked | 500 Gallons | X | X | 0 | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS |  | Pump house product recovery tank
| 264 | Pump House | 264 Pump house | Electrical Equipment | Automatic Gate (west) |  | Tymetal gate systems | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Automatic Gate (West)
| 264 | Pump House | 264 Pump house | Electrical Equipment | Automatic Gate |  | Tymetal | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Automatic Gate (east)
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump house vent switch |  | Appleton Electric Co | DS454 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Vent switch
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump house vent switch |  | Appleton Electric Co | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Vent switch
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump 5 switch |  | Cooper Crouse Hines | FLS30 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump 6 switch |  | Cooper Crouse Hines | FLS30 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump control switches-offload#3 |  | Killark | FXCS-0A15D | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump control switches-offload #3
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump control switches-offload#2 |  | Killark | FXCS-0A15D | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump control switches-offload#2
| 264 | Pump House | 264 Pump house | Electrical Equipment | Gate switch |  | YK | LR 63663 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Gate switch rear
| 264 | Pump House | 264 Pump house | Electrical Equipment | Gate switch |  | YK | PBS-3 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Gate switch front
| 264 | Pump House | 264 Pump house | Electrical Equipment | Gate switch |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump house vent fan located on roof not accessible without ladder
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump control switches-off load#1 |  | Killark | FXCS-0A15D | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump control switches-offload #1
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump 2 switch |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump 2 switch
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump#1-Power switch |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Pump#1-Power Switch
| 264 | Pump House | 264 Pump house | Electrical Equipment | 220V electrical panel |  | Nelson Electric | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 220V electrical panel-pump room office
| 264 | Pump House | 264 Pump house | Electrical Equipment | Scully |  | Scully | ST-15-115-WX6 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Alarm panel pump house
| 264 | Pump House | 264 Pump house | Electrical Equipment | Heart era electrical panel |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Heaters electrical panel
| 264 | Pump House | 264 Pump house | Electrical Equipment | Offload pump pannel |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Offload pump panel
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump 1 & 3 panel |  | Eaton | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Issue stand pump 1 & 3
| 264 | Pump House | 264 Pump house | Electrical Equipment | Electrical Panel A- Pump room office |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel A
| 264 | Pump House | 264 Pump house | Electrical Equipment | Switch |  | Eaton | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Issue stand 2 pump panel
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump 5 panel |  | Eaton | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 receipt pump 5 panel
| 264 | Pump House | 264 Pump house | Electrical Equipment | Electrical panel B |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel B-pump room office
| 264 | Pump House | 264 Pump house | Electrical Equipment | Pump 6 control panel |  | Eaton | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 264 receipt pump 6 control panel
| 264 | Pump House | 264 Pump house | Electrical Equipment | Main electrical disconnect |  | Westinghouse | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Main power disconnect
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Pump Ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Pump house product recovery tank ground
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Ground reel/static grounding-off load #3 |  | Hannay Reels | HGR 50-50 | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Ground Reel/static grounding-offload #3
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Ground Rod / Corner of Building |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Pump house static ground
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Gound Rod / Side of Building |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Pump house electric equipment ground
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Ground reel/static grounds-offload #2 |  | Hannay Reels | HGR-5050 | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Ground reel/static grounds-offload #2
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Ground reels/static grounding |  | Hannay Reels | HGR 50-50 | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Ground reels/static grounding-offload#1
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Static ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Pump house product recovery tank ground
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Static ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Pump house static ground
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Scully groundhog |  | Scully groundhog | ST-47-ELK | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 264 offload 1
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Barton tank system ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Barton tank gauge system ground point
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Scully Groundhog-offload #3 |  | Scully | Groundhog | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Scully Groundhog-offload #3
| 264 | Pump House | 264 Pump house | Static Grounding Systems | Scully groundhog-offload #2 |  | Scully | Groundhog | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Scully Groundhog-offload. #2
| 264 | Pump House | 264 Pump house | Electric Motors | Pump 5 motor |  | Teco Westinghouse | E84757 | 230/460 | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS |  | 264 pump 5 line
| 264 | Pump House | 264 Pump house | Electric Motors | Pump 6 motor |  | Teco Westinghouse | E84757 | 230/460 | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS |  | 264 pump 6 line
| 264 | Pump House | 264 Pump house | Electric Motors | Pump 2 motor |  | Taco Westinghouse | E84757 | 230/460 | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS |  | Pump 2 motor
| 264 | Pump House | 264 Pump house | Electric Motors | Pump #1-Motor |  | Yes o/Westinghouse | E84757 | 230/460 | X | X | X | 9-1.7 | (1) Inadequate ventilation or air flow (2) Unbalanced voltage or an overload (3) Bearing failure (4) Insulation failure (5) Shaft misalignment | No Operator Requirement | Partial System OOS |  | Pump #1 -Motor
| 264 | Pump House | 264 Pump house | Lighting | Perimeter Lighting-Fac 264 |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Perimeter Lighting-Fac#264 5 poles-7 lights
| 264 | Pump House | 264 Pump house | Lighting | Facility Lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Facility Lighting-8 inside pump house. 2 on exterior (North side)
| 264 | Pump House | 264 Pump house | Cathodic Protection | Cathodic protection |  | Fairyland Electric Industries | #11937 | N/A | X | X | X | 9-2.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 9 Catholic protection devices inside pump room
| 264 | Pump House | 264 Pump house | Containment Systems | Perimeter Fencing-Fac 264 |  | N/A | N/A | N/A | 0 | 0 | 0 | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Perimeter Fencing-Fac 264
| 264 | Pump House | 264 Pump house | Containment Systems | Spill containment-Fac 264 |  | N/A | N/A | N/A | 0 | 0 | 0 | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Spill containment-Fac 264
| 264 | Pump House | 264 Pump house | Containment Systems | Bollards-12 |  | N/A | N/A | N/A | 0 | 0 | 0 | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Bollards-12
| 265 | Bulk storage tank | 265 Bulk storage tank | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 265 | Bulk storage tank | 265 Bulk storage tank | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 265 | Bulk storage tank | 265 Bulk storage tank | Centrifugal Pumps | Pump |  | Corcoran | 2000D | 0-15 GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact |  | PRT tank 265 pump
| 265 | Bulk storage tank | 265 Bulk storage tank | General System Control Valves | Tk 265 receipt line control valve |  | Cal-Val | PN16 | 8.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Tank 265 Receipt Line
| 265 | Bulk storage tank | 265 Bulk storage tank | General System Control Valves | Tk 265 high level float valve |  | Cal-Val | C4-983 | 1.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Cla Val high level float valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Thermal and/or Pressure Relief Valves | Tk 265 receipt line PRV |  | Taylor | 82E375131-10-10-0 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | Tank 265 receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Thermal and/or Pressure Relief Valves | Tk 265 issue PRV |  | Taylor | 82E375131-10-10-0 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | Tank issue PRV with test port
| 265 | Bulk storage tank | 265 Bulk storage tank | Low Point Drains | Tk 265 Low Point 1 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | 265 low point
| 265 | Bulk storage tank | 265 Bulk storage tank | Low Point Drains | Tk 265 Low Point 2 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | 265 Low Point -#2
| 265 | Bulk storage tank | 265 Bulk storage tank | Sight Flow Indicators | Saver tank sight glass |  | N/A | N/A | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | Sight glass prt
| 265 | Bulk storage tank | 265 Bulk storage tank | Gate Valves | Sight glass iso valve |  | Schnitzer | 300 lb | 0.5 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | Sight glass valve or tank
| 265 | Bulk storage tank | 265 Bulk storage tank | Gate Valves | Tk 265 dike drain valve |  | Tufline | Painted / Illegible | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | TK# 265Dike Drain-Gate Valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank issue PRV Iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Issue PRT iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Test port |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Low point ball valve 1 |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 265 low point ball valve 1
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | High point vent top of dike will receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Apollo | 800W00 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | ISO valve or tank
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Apollo | 800W00 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | ISO valve or tank
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Hi hi valve chamber iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Hi level iso lower chamber
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Hi level chamber drain valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Hi level float iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Cla Val float valve iso bottom
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | High point vent issue line top of dike wall
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Apollo | 800W00 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | ISO valve PR Tank
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Issue PRV test port iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | Painted / Not Legible | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Issue line high point vent iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 low low level control
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 low level chamber release
| 265 | Bulk storage tank | 265 Bulk storage tank | Ball Valves | Ball valve |  | C&C | 1-2000 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 265 low level control
| 265 | Bulk storage tank | 265 Bulk storage tank | Double Block and Bleed Valves | Tk 265 receipt DBB valve |  | Truseal | 1-306R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Tank 265 receipt line
| 265 | Bulk storage tank | 265 Bulk storage tank | Double Block and Bleed Valves | Tk 265 issue line DBB valve |  | Truseal | 1-306R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Issue tank iso valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Double Block and Bleed Valves | Crossover DBB valve |  | Truseal | 1-306R | 6.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Crossover valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Globe Valves | Tk 265 bottom drain globe valve |  | FS | 96181 | 2.0 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | Tank bottom drain
| 265 | Bulk storage tank | 265 Bulk storage tank | Globe Valves | Saver tank iso globe valve |  | Schnitzer | 300 lb | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | Sight glass iso valve prt
| 265 | Bulk storage tank | 265 Bulk storage tank | Check Valves | Check Valve |  | Stockman | Stockman | 1.0 in. | X | X | 0 | 6-6.2.8 | Visual for damage, leaks, tightness. | No Operator Requirement | Partial System OOS |  | PRT check valve
| 265 | Bulk storage tank | 265 Bulk storage tank | Concrete and Cement Brick Dike/Berm Walls and Floors | Tank 265 dike |  | N/A | N/A | N/A | 0 | 0 | 0 | 8-10.2 | No Manufacturer Requirements Available | Daily - Inspect for vegetation that has taken root in seals or cracks. All vegetation shall be removed in all cases to prevent penetration of seals, joints or cracks in the concrete. Inspect walls constructed of bricks for signs of deterioration (e.g., spalling caused by freeze-thaw conditions, cracks, and joint cracks between bricks). Walls constructed of bricks shall be patched immediately to prevent further penetration of the wall structure. | No Mission Impact |  | Tank 265 dike
| 265 | Bulk storage tank | 265 Bulk storage tank | Aboveground Field-Erected Tanks | Tank 265 |  | Tank Consultant Mechanical | Floating roof with geodesic dome | 252,000 Gallons | 0 | 0 | X | 8-4 | No Manufacturer Requirements Available | Monthly - Visually inspect for evidence of leaks; shell distortions; signs of settlement; corrosion, condition of tank foundation, condition of coating, insulation systems, and appurtenances. Inspection shall include all components and equipment located inside the containment area such as piping, pipe supports, containment valves, and product saver tanks. Items noted during the inspection will be documented for follow-up action by an authorized inspector. See Appendix F for the Field-Erected Tank Monthly Inspection Checklist. Visually inspect chime to ringwall sealant. Seal should be maintained in good working order to prevent corrosion of the underside of the tank bottom. | Partial System OOS
| 265 | Bulk storage tank | 265 Bulk storage tank | Geodesic Dome Roofs | Tank 265 |  | N/A | N/A | N/A | 0 | 0 | X | 8-4.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact
| 265 | Bulk storage tank | 265 Bulk storage tank | Product Saver Tanks | Tk 265 Product saver tank |  | GTP | Unmarked | 50 Gallons | X | X | 0 | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS |  | Product recovery tank
| 265 | Bulk storage tank | 265 Bulk storage tank | Mechanical Tape Gauges | Tank tape gauge |  | Shane & Jurs | 92021 | N/A | X | X | 0 | 8-9.7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Automatic tank gauge under CMP
| 265 | Bulk storage tank | 265 Bulk storage tank | Electrical Equipment | PRT pump switch |  | Red Dot | EFD-T12 | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Power Switch PRT
| 265 | Bulk storage tank | 265 Bulk storage tank | Electrical Equipment | Electrical Panels-Bulk Storage Lighting |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panels-Bulk Storage
| 265 | Bulk storage tank | 265 Bulk storage tank | Electrical Equipment | Electrical panel-Bulk storage |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical panel-Bulk Storage
| 265 | Bulk storage tank | 265 Bulk storage tank | Static Grounding Systems | Stairwell ground strap |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Tank 265 stairwell ground strap
| 265 |  |  | Static Grounding Systems | Tank ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Tank 265 ground
| 265 | Bulk storage tank | 265 Bulk storage tank | Static Grounding Systems | PRT tank ground cable |  | 65 | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Tank 265 PRT ground
| 265 | Bulk storage tank | 265 Bulk storage tank | Static Grounding Systems | Thanks vents ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 409 tank vent ground
| 265 | Bulk storage tank | 265 Bulk storage tank | Lighting | Bulk Storage-Perimeter Lighting |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Bulk Storage-Perimeter Lighting-6 poles, 8 lights
| 265 | Bulk storage tank | 265 Bulk storage tank | Fire Protection Systems | Fire suppression line |  | N/A | N/A | N/A | X | X | 0 | Fire Protection Systems | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Fire suppression line to tank
| 267 | Bulk storage tank | 267 Bulk storage tank | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 267 | Bulk storage tank | 267 Bulk storage tank | Centrifugal Pumps | PRT Pump |  | Not Labeled | XLF1 25B | 50 GPM GPM/SCFM | X | X | X | 3-8.1 | During routine pump inspections only the easy to monitor factors such as pressure, temperature, vibration etc can be checKed. But during quarterly inspections, shaft alignment and oil levels should also be checked. Change Oil Annually | No Operator Requirement | No Mission Impact |  | PRT Pump
| 267 | Bulk storage tank | 267 Bulk storage tank | General System Control Valves | High level shut off calve |  | Cal-Val | 413-01-112C | 8.0 in. | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | High level shut off valve
| 267 | Bulk storage tank | 267 Bulk storage tank | General System Control Valves | High level float control valve |  | Cal-Val | 2371011 | N/A | X | X | X | 4-3.2.1 | No Manufacturers Data Available. Adjustment not advised unless formal training is received. | No Operator Requirement | Partial System OOS |  | Tank 267 high level float control
| 267 | Bulk storage tank | 267 Bulk storage tank | Thermal and/or Pressure Relief Valves | PRV |  | Taylor | 83E3751311-10-10-0 | 1.0 in. 51 - 100 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | Receipt PRV
| 267 | Bulk storage tank | 267 Bulk storage tank | Thermal and/or Pressure Relief Valves | Issue PRV |  | Taylor | 825E3751311-10-10-0 | 1.0 in. 51 - 125 PSI | X | X | X | 6-6.3 | Thermal and pressure relief valves shall be validated for proper calibration by isolating the valve and using the test connection provided on the piping in conjunction with a hand pump and portable reservoir. The operating pressure shall be checked against the set pressure listed on the stamped information plate attached to the valve. The operating pressure shall be adjusted to the stamped set pressure if necessary. | No Operator/equipment Requirements | Partial System OOS |  | Issue PRV
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drain Pits | Low point pit 267 |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-11.4 | No Manufacturer Requirements Available | Monthly - Inspect low point drain pits to ensure they are dry and free of water and other debris and that all pit and piping components are leak free and in good working condition. Inspect the pit for fuel or water. Fuel or water found in the pit shall be sumped out as soon as possible. Check pipe penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no water seepage into the pits. Check pit lid seals for deterioration and replace as necessary. Ensure that low point vent valves, quick-disconnect couplings or pit lids are lockable and that locking mechanisms are in good working order. Inspect low point drain pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS |  | Low point pit 267
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drain Pits | LowPoint pit 267 |  | N/A | N/A | N/A | 0 | 0 | 0 | 6-11.4 | No Manufacturer Requirements Available | Monthly - Inspect low point drain pits to ensure they are dry and free of water and other debris and that all pit and piping components are leak free and in good working condition. Inspect the pit for fuel or water. Fuel or water found in the pit shall be sumped out as soon as possible. Check pipe penetrations through pit wall or bottom to ensure that mechanical seals and boot seals are in good working condition and are allowing no water seepage into the pits. Check pit lid seals for deterioration and replace as necessary. Ensure that low point vent valves, quick-disconnect couplings or pit lids are lockable and that locking mechanisms are in good working order. Inspect low point drain pit bonding cables for corrosion and ensure electrical continuity between bonded equipment. | Partial System OOS |  | Low point pit 267
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drains | Low point drain #2 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | Low point #2
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drains | 267 low point drain 2 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | 267 low point drain 2
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drains | Low point 267 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | Low point 267
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drains | Low point 267 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | Low point 267
| 267 | Bulk storage tank | 267 Bulk storage tank | Low Point Drains | Low point drain 2 |  | Flow -Tek | RF15 | N/A | 0 | 0 | 0 | 6-12.1 | No Manufacturer Requirements Available. Refere to requirement of installed equipment at each loacation. | Weekly - Visually inspect low point drains. Ensure that quick-disconnect dust caps are in place and that valves are locked closed. Monthly or as required by local conditions. Verify low point drains are closed after maintenance. Operate low point drains when system is not under operating pressure. If there is an absence of sufficient line pressure close the low point drain and pressurize the system. Once adequate pressure is available, continue draining until the piping fuel sample is clear and bright with no visible water. | Partial System OOS |  | 267 low point 2
| 267 | Bulk storage tank | 267 Bulk storage tank | Sight Flow Indicators | Sight glass |  | N/A | N/A | .5 In. | 0 | 0 | 0 | 6-12.3 | Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Daily or at each use - Verify there are no leaks around pipe connection fittings and glass seals. Also check glass for indications of cracks. | Partial System OOS |  | Tank 267 prt line
| 267 | Bulk storage tank | 267 Bulk storage tank | Gate Valves | Tk 267 dike drain valve |  | Tufline | Painted / Illegible | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | TK#267-Dike Drain-Gate Valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15-1 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 prt line
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF15-1 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 prt line
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Receipt PRV iso valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Receipt PRV iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF15 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 low level valve. Unhooked
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF15-1 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 low low level valve. Unhooked
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Issue line PRV iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 interstitial bottom valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 interstitial bottom valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF-15 | 1.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 interstitial bottom valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Flow -Tek | RF15-1 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 interstitial bottom valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Issue PRV iso valve |  | Flow -Tek | RF-15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Issue PRV iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point drain ball valve 1 |  | Flow -Tek | RF15 | 2.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low point ball valve 1-267
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | PRV test port valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank receipt PRV test port valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | PRT drain |  | Ball Valve | RF15 | 0.75 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Ball Valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point ball valve 1 |  | Watts | 1000 WOG | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 267 low point drain 1
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point drain ball valve |  | Watts | 1000 WOG | 2.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 267 low point ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point drain ball valve #1 |  | Watts | 1000 WOG | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low point drain ball valve #1
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low level iso valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low level iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low low level iso valve |  | Nibco | CWB | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low low level iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Issue PRV test port iso valve |  | Gammon | GTP-1149 | 0.25 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Issue PRV Test port iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point #2 ball valve |  | Painted / Not Legible | Painted / Not Legible | 2.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low point -Ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point 2 ball valve |  | Painted / Not Legible | Painted / Not Legible | 2.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 267 low point ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Low point 2 Ball valve |  | Painted / Not Legible | Painted / Not Legible | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 267 low point ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 high level float iso ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 high level float iso ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 high level chamber high iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Nibco | WCB | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 chamber high high iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Apollo | RF15 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Receipt line PRV iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Drain Line |  | C&C | 1-2000 | 0.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Low level drain valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | 267 Low point drain ball valve |  | Painted / Not Legible | Painted / Not Legible | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 267 Low point line drain ball valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Ball valve | 316 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 prt line
| 267 | Bulk storage tank | 267 Bulk storage tank | Ball Valves | Ball valve |  | Ball valve | 316 | 1.0 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Tank 267 prt line
| 267 | Bulk storage tank | 267 Bulk storage tank | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 2.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Tank 267 prt line
| 267 | Bulk storage tank | 267 Bulk storage tank | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 4.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Tank valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-306R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Receipt tank iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Double Block and Bleed Valves | Double block and bleed |  | Truseal | 1-303R | 8.0 in. | X | X | X | 6-6.2.5 | Valve design must permit sealing slips to be replaced from the bottom with the valve mounted in the piping. Valves must operate from fully open to fully closed by rotation of the handwheel to lift and turn the plug. | No Operator Requirement | Partial System OOS |  | Tank issue line iso valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Globe Valves | Globe valve |  | Kenco | Not Marked | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | Tank 267 prt sight glass valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Globe Valves | Globe valve |  | Kenco | Not Marked | 0.5 in. | X | X | 0 | 6-6.2.7 | 1. Regular inspection of the valve. ... 2. If the valve is not operated regularly it is a good idea to cycle the valve to ensure the disc is not bedding itself in the seat. 3. Grease the crossbar by using a grease gun on the grease nipple provided. ... 4. Slightly tighten the gland bolts if the packing needs adjustment. | No Operator Requirement | Partial System OOS |  | Tank 267 prt sight glass valve
| 267 | Bulk storage tank | 267 Bulk storage tank | Aboveground Field-Erected Tanks | Tank 267 |  | Cape | Floating roof with geodesic dome | 630,000 Gallons | 0 | 0 | X | 8-4 | No Manufacturer Requirements Available | Monthly - Visually inspect for evidence of leaks; shell distortions; signs of settlement; corrosion, condition of tank foundation, condition of coating, insulation systems, and appurtenances. Inspection shall include all components and equipment located inside the containment area such as piping, pipe supports, containment valves, and product saver tanks. Items noted during the inspection will be documented for follow-up action by an authorized inspector. See Appendix F for the Field-Erected Tank Monthly Inspection Checklist. Visually inspect chime to ringwall sealant. Seal should be maintained in good working order to prevent corrosion of the underside of the tank bottom. | Partial System OOS |  | Tank 267
| 267 | Bulk storage tank | 267 Bulk storage tank | Geodesic Dome Roofs | Tank 267 |  | N/A | N/A | N/A | 0 | 0 | X | 8-4.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 267 bulk storage tank geodesic some
| 267 | Bulk storage tank | 267 Bulk storage tank | Product Saver Tanks | 267 Product recovery tank |  | Schultz | SC-9000-15-SW | 55 Gallons | X | X | 0 | 8-9.10 | No Manufacturer Requirements Available | No Operator Requirement | Partial System OOS |  | Product Recovery Tank
| 267 | Bulk storage tank | 267 Bulk storage tank | Mechanical Tape Gauges | Automatic tank gauge |  | Shand & Jura | 92021 | N/A | X | X | 0 | 8-9.7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Automatic tank gauge
| 267 | Bulk storage tank | 267 Bulk storage tank | Electrical Equipment |  |  | Appleton Electric Co | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | PRT- Pump Switch
| 267 | Bulk storage tank | 267 Bulk storage tank | Static Grounding Systems | Tank 267-Grounding |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Tank 267-Ground
| 267 | Bulk storage tank | 267 Bulk storage tank | Fire Protection Systems | Fire suppression tank 267 |  | N/A | N/A | N/A | X | X | 0 | Fire Protection Systems | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Fire suppression tank 267
| 404 | Liquid fuel load/Unload area | 404 Liquid fuel load/unload area | Fuel Truck Containment Areas | Service station load/offload |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Service station load/offload area
| 407 | Mogas operating storage tank | Mogas operating storage tank | Remote Dispenser Pumps | 407 Mogas pump |  | Red Jacket | Not Legible | GPM/SCFM | X | X | 0 | 7-15.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Mogas pump
| 407 | Mogas operating storage tank | Mogas operating storage tank | Underground Double-walled Shop-Fabricated Tanks | 407 Mogas tank |  | Unknown | Unknown | 12000 Gallons | X | X | X | 8-5.4.2 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-4): Ensure all tank port covers are present, are in good condition, and seated firmly on the correct tank. Inspect tank stick gauge and ensure markings are legible and that the stick gauge is not warped or broken. Inspect tank for water using ATG or stick gauge with water-finding paste. Remove water found in tank. Open and inspect tank-top containment sumps and ensure no fuel or water is collected in the sumps. Check for and remove obstructions in tank fill pipe. | Partial System OOS |  | Mogas tank
| 407 | Mogas operating storage tank | Mogas operating storage tank | Tank Pressure/ Vacuum Vents | Mogas tank vent |  | OPW | 523V | 2.0 In. | 0 | 0 | X | 8-9.3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 407 mogas vent
| 408 | Diesel operating storage tank | Diesel operating storage tank | Remote Dispenser Pumps | 408 Diesel pump |  | Red jacket | Not Legible | GPM/SCFM | X | X | 0 | 7-15.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 408 diesel pump
| 408 | Diesel operating storage tank | Diesel operating storage tank | Underground Double-walled Shop-Fabricated Tanks | 408 Diesel tank |  | Unknown | Unknown | 12000 Gallons | X | X | X | 8-5.4.2 | No Manufacturer Requirements Available | Monthly - Monthly External Inspection (Identified as P in Table 8-4): Ensure all tank port covers are present, are in good condition, and seated firmly on the correct tank. Inspect tank stick gauge and ensure markings are legible and that the stick gauge is not warped or broken. Inspect tank for water using ATG or stick gauge with water-finding paste. Remove water found in tank. Open and inspect tank-top containment sumps and ensure no fuel or water is collected in the sumps. Check for and remove obstructions in tank fill pipe. | Partial System OOS |  | diesel tank
| 408 | Diesel operating storage tank | Diesel operating storage tank | Tank Pressure/ Vacuum Vents | Diesel tank vent |  | OPW | 23 Series | 2.0 In. | 0 | 0 | X | 8-9.3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 408 diesel tank vent
| 409 | Military service station | 409 Military service station | Canopies | Canopy |  | N/A | N/A | N/A | X | X | 0 | 11-2.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 408 canopy
| 409 | Military service station | 409 Military service station | Emergency Eyewash/Showers | Emergency Eyewash-MSS |  | Haws | Unmarked | 2.0 In. | X | X | X | 11-3 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Emergency Eyewash-MSS
| 409 | Military service station | 409 Military service station | Signage and Markings | Signage and markings |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Signage and markings
| 409 | Military service station | 409 Military service station | Gate Valves | Containment drain valve |  | Glow Kennedy | 2945A | 6.0 in. | X | X | 0 | 6-6.2.3 | Operate from fully open to fully closed . Conduct Tightness test as required for application. | No Operator Requirement | Partial System OOS |  | 409 drain valve
| 409 | Military service station | 409 Military service station | Ball Valves | Mogas pump discharge iso valve |  | Velan | RF15 | 2.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | Mogas Pump discharge
| 409 | Military service station | 409 Military service station | Ball Valves | Diesel pump ball valve |  | Painted / Not Legible | Painted / Not Legible | 2.5 in. | X | X | 0 | 6-6.2.4 | Operate from fully open to fully closed with 90 degree rotation of the ball. | No Operator Requirement | No Mission Impact |  | 409 diesel
| 409 | Military service station | 409 Military service station | Differential Pressure Gauges | F/S 1 DP gauge |  | Schultz | SC-5150-30 | 0 - 0 PSI | X | X | X | 6-7.2 | Periodic calibration of this instrument is unnecessary because the graduated scale is made to match the characteristics (load/deflection curve) of the spring. If the spring loses some of its strength for some reason, the ”free length” must be shortened. Afull length spring will always provide accurate readings. This is a fundamental truth about compression springs. This spring is at its “free full length” when there is zero differential pressure; the top of the piston is then in the “zero” band of the graduated scale. | Quarterly - Clean outside of gauge glass. | Partial System OOS |  | F\S 1 DP gauge
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 1 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 2 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 7 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 6 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | Dispenser 6 strainer
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 5 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | Dispenser 5 strainer
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 3 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | Strainer-Dispenser cabinet 3
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 4 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | Strainer-dispenser cabinet 4
| 409 | Military service station | 409 Military service station | Dispenser Strainers | Dispenser 8 strainer |  | Vacuo Maximo | 200427 | 20CMHG | 0 | 0 | X | 7-10 | Inspect strainer cover gasket for cracks, distortion, and dry rot. | No Operator Requirement | Partial System OOS |  | Dispenser 8 strainer
| 409 | Military service station | 409 Military service station | Emergency Shutoff Valves | Dispenser 1/2 fire valve |  | OPW | OPW10BHMP5830 | 1.5 in. | 0 | 0 | X | 7-12 | Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. Inspect mechanical links of the valve for correct operation. Conduct test of valve to ensure it operates correctly. | Monthly - Inspect stabilizer bar to ensure that it is securely mounted below the base of the dispenser. Inspect the mounting bolts that secure the emergency shutoff valve to the stabilizer bar. Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Emergency Shutoff Valves | Dispenser 5/6 fire valve |  | OPW | OPW10BHMP5830 | 1.5 in. | 0 | 0 | X | 7-12 | Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. Inspect mechanical links of the valve for correct operation. Conduct test of valve to ensure it operates correctly. | Monthly - Inspect stabilizer bar to ensure that it is securely mounted below the base of the dispenser. Inspect the mounting bolts that secure the emergency shutoff valve to the stabilizer bar. Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. | Partial System OOS |  | Dispenser 5/6 sheer valve
| 409 | Military service station | 409 Military service station | Emergency Shutoff Valves | Dispenser 3/4 fire valve |  | OPW | OPW10BHMP5830 | 1.5 in. | 0 | 0 | X | 7-12 | Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. Inspect mechanical links of the valve for correct operation. Conduct test of valve to ensure it operates correctly. | Monthly - Inspect stabilizer bar to ensure that it is securely mounted below the base of the dispenser. Inspect the mounting bolts that secure the emergency shutoff valve to the stabilizer bar. Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. | Partial System OOS |  | Fire valve -Dispenser cabinet 3&4
| 409 | Military service station | 409 Military service station | Emergency Shutoff Valves | Dispenser 7/8 fire valve |  | OPW | OPW10BHMP5830 | 1.5 in. | 0 | 0 | X | 7-12 | Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. Inspect mechanical links of the valve for correct operation. Conduct test of valve to ensure it operates correctly. | Monthly - Inspect stabilizer bar to ensure that it is securely mounted below the base of the dispenser. Inspect the mounting bolts that secure the emergency shutoff valve to the stabilizer bar. Inspect fusible link and ensure it is not obstructed. Ensure valve body is clean and free of fuel. | Partial System OOS |  | Dispenser 7/8 fire valve
| 409 | Military service station | 409 Military service station | Dispenser Sumps | Dispenser 1/2 sump |  | Unmarked | Unmarked | N/A | X | X | X | 7-13 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Sumps | Dispenser 3/4 sump |  | Unmarked | Unmarked | N/A | X | X | X | 7-13 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS |  | Dispenser 5/6 sump
| 409 | Military service station | 409 Military service station | Dispenser Sumps | Dispenser 3/4 sump |  | Unmarked | Unmarked | N/A | X | X | X | 7-13 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS |  | Dispenser 3&4 sump
| 409 | Military service station | 409 Military service station | Dispenser Sumps | Dispenser 7/8 sump |  | Unmarked | Unmarked | N/A | X | X | X | 7-13 | Inspect sump pipe transition fittings for tears, cracks, or other signs of deterioration. Test sumps and ensure they are liquid tight by using vacuum, pressure, or liquid testing in accordance with 40 CFR 280, Section 43. | Monthly - Inspect for signs of water, fuel, trash, and debris inside sumps. Remove and properly dispose of collected water, fuel, trash, and debris. Visually inspect penetration fittings. If fuel or water is detected investigate the source and repair. | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | EFSO Systems | EFSO-MSS |  | Schnieder | Unmarked | N/A | X | X | 0 | 7-16 | Proper operation, box seals for integrity. Electrical connections for continuity. | No Operator Requirement | Partial System OOS |  | EFSO-MSS
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 2 nozzle |  | OPW | 11BP100517580 | 0.75 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 3 nozzle |  | OPW | 7HB-0100 | 1.0 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser Nozzle-#3
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 4 nozzle |  | OPW | 7HB-0100 | 1.0 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser Nozzle-#4
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 1 nozzle |  | OPW | 11BP100517618 | 0.75 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 6 nozzle |  | OPW | 11BP100517619 | 0.75 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser 6 nozzle
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 5 nozzle |  | OPW | 11BP100517622 | 0.75 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser 5 nozzle
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 7 nozzle |  | OPW | 7HB-0100 | 1.0 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Nozzles | Dispenser 8 nozzle |  | OPW | 7HB-0100 | 1.0 in. | 0 | 0 | X | 7-2 | Start flow into approved test container; place nozzle in low clip position. Immerse nozzle spout tip in the gasoline in the approved test container. The nozzle tip must be at least three (3) inches from the bottom of the container to prevent back-pressure in the spout. Nozzle must shut off five consective tests. | Daily - Inspect dispenser nozzle spout. Ensure it is tight, round, has no cracks, or excessive wear. Inspect automatic shutoff hole. Ensure the hole is open and free of obstructions. Inspect nozzle hold-open latch. Ensure the latch is straight, moves freely, and the return spring operates correctly. Inspect body of nozzle. Ensure the body is in good condition and that the valve stem is clean and free of fuel. Inspect the nozzle to hose connection and ensure it is clean and free of fuel. Monthly - Dispenser nozzle handles shall be inspected for an expiration date established by the manufacturer. Nozzles must be replaced before the indicated expiration date. | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 2 hose |  | Black Snake | 544A | 0.75 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 3 hose |  | Black Snake | 544A | 1.0 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | Dispenser Hose-#3
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 4 hose |  | Black Snake | 544A | 1.0 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | Dispenser Hose-#4
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 1 hose |  | Black Snake | 544A | 0.75 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 5 hose |  | Black Snake | 544A | 0.75 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | Dispenser 5 hose
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 6 hose |  | Black Snake | 544A | 0.75 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | Dispenser 6 hose
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 8 hose |  | Black Snake | 544A | 1.0 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Hoses | Dispenser 7 hose |  | Black Snake | 544A | 1.0 in. | 0 | 0 | 0 | 7-3 | Check for expiration date, and physical condition/damage leaks. | Daily - Inspect dispenser hoses and hose whips for gouges, cuts, blisters, or outside wear that may lead to rupture during use. Replace hose or hose whips that show signs of wear. Inspect connection points of hoses and hose whips to the dispenser, breakaways, swivels, and the nozzle and ensure the connection points are clean and free of fuel. | Partial System OOS |  | Dispenser 7 hose
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 2 breakaway |  | OPW | 66REC | 0.75 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 1 breakaway |  | OPW | 66REC | 0.75 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 6 breakaway |  | OPW | 66REC | 0.75 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | Dispenser 6 breakaway
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 5 breakaway |  | OPW | 66REC | 0.75 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | Dispenser 5 breakaway
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 3 breakaway |  | OPW | 66REC | 1.0 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | Breakaway-Pump#3
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 4 breahaway |  | OPW | 66REC | 1.0 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | Breakaway-Pump #4
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 7 breakaway |  | OPW | 66RB | 1.0 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Breakaways | Dispenser 8 breakaway |  | OPW | 66RB | 1.0 in. | 0 | 0 | 0 | 7-4 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect breakaways for loose connections and signs of damage to poppets. Ensure breakaways are clean and free of fuel. Monthly - Inspect breakaway for an expiration date established by the manufacturer. Breakaways must be replaced before the indicated expiration date. | No Mission Impact |  | Dispenser 8 breakaway
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 2 swivel |  | OPW | 45-5060 | 0.75 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 1 swivel |  | OPW | 45-5060 | 0.75 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 5 swivel |  | OPW | 45-5060 | 0.75 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser 5 swivel
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 6 swivel |  | OPW | 45-5060 | 0.75 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser 6 swivel
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 4 swivel |  | OPW | 241TPS-1000 | 1.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser swivel-Pump#3
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 3 swivel |  | OPW | 241TPS-1000 | 1.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | Dispenser Swivel-Pump#4
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 7 swivel |  | OPW | 241TPS-1000 | 1.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Swivels | Dispenser 8 swivel |  | OPW | 241TPS-1000 | 1.0 in. | 0 | 0 | 0 | 7-5 | Inspect for expiration date. Inspect for loose connections and signs of damage. | Daily - Inspect swivel for loose connections and signs of damage. Ensure swivel rotates easily and is clean and free of fuel. Monthly - Inspect swivel for expiration date established by manufacturer. Swivels must be replaced before the indicated expiration date. | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 8 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 8 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 7 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 7 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 6 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 6 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 5 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 5 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 4 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 4 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 3 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 3 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 2 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 2 hose retriever
| 409 | Military service station | 409 Military service station | Hose Retriever | Dispenser 1 hose retriever |  | OPW | 211899 | N/A | 0 | 0 | 0 | 7-6 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser 1 hose retriever
| 409 | Military service station | 409 Military service station | Dispenser Cabinet | Dispenser cabinet 1/2 |  | Wayne | G6202D/2GJK/W1 | N/A | 0 | 0 | X | 7-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Cabinet | Dispenser cabinet-3/4 |  | Wayne | G6202D/2GJK/W1 | N/A | 0 | 0 | X | 7-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser Cabinet-3&4
| 409 | Military service station | 409 Military service station | Dispenser Cabinet | Dispenser cabinet 7/8 |  | Wayne | G6202D/2GJK/W1 | N/A | 0 | 0 | X | 7-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 408 cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Cabinet | Dispenser cabinet 5/6 |  | Wayne | G6202D/2GJK/W1 | N/A | 0 | 0 | X | 7-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Dispenser cabinet 5/6
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 5 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Dispenser meter 5
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 6 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Dispenser meter 6
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 7 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Dispenser Meter-Pump#8
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 8 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Dispenser Metter-Pump#8
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 4 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Dispenser Meter-#4
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 3 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Dispenser Meter -#3
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 2 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Meters | Dispenser 1 meter |  | Wayne | 2PM-6 | 0-15 GPM/SCFM | 0 | 0 | X | 7-8 | Inspect for damage, smooth operation and legibility. | Monthly - Inspect meter and ensure meter is clean and free of fuel. Ensure calibration mechanism is sealed. | Partial System OOS |  | Cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 5 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | Dispenser 5 filter
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 2 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 6 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | Dispenser 6 filter
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 3 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | Dispenser Filter-#3
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 1 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | 409 dispenser cabinet 1
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 4 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | Dispenser Filter -#4
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 7 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | 409 cabinet 7/8
| 409 | Military service station | 409 Military service station | Dispenser Filters | Dispenser 8 filter |  | Wayne | 70104 | 400BMG-10 | 0 | 0 | X | 7-9 | Check exterior for damage | No Operator Requirement | Partial System OOS |  | Dispenser 8 filter
| 409 | Military service station | 409 Military service station | Externally Mounted Level Alarms | Exterior Alarm |  | Veeder-Root | Unmarked | N/A | 0 | 0 | 0 | 8-9.9.1 | Lift the manual test lever of internally mounted float valve (if equipped). Ensure that the HLSO closes when the float of the float valve is raised. | No Operator Requirement | Partial System OOS |  | Exterior Alarm
| 409 | Military service station | 409 Military service station | Internally Mounted Level Alarms | Tank Monitoring stystem |  | Owens Corning | SB0014C1 | N/A | 0 | 0 | X | 8-9.9.3 | Lift the manual test lever of internally mounted float valve (if equipped). Ensure that the HLSO closes when the float of the float valve is raised. | No Operator Requirement | Partial System OOS |  | Tank Monitoring System-MSS
| 409 | Military service station | 409 Military service station | Electrical Equipment | Electrical Panel-Air compressor |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel-Air compressor
| 409 | Military service station | 409 Military service station | Electrical Equipment | Electrical Panel-Compressor room |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel-Compressor room
| 409 | Military service station | 409 Military service station | Electrical Equipment | Electrical Panel 1B |  | Unmarked | Unmarked | N/A | X | X | 0 | 9-1.2 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Electrical Panel 1B
| 409 | Military service station | 409 Military service station | Static Grounding Systems | Static ground |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | Statics Ground
| 409 | Military service station | 409 Military service station | Static Grounding Systems | 409 bldg ground cable |  | N/A | N/A | N/A | X | X | X | 9-1.6.2 | Measure the ground resistance with an instrument designed specifically to measure and document earth/ground resistance, soil resistivity, and current flow. Conduct the test by using the fall-of-potential method as described in the Institute of Electronic and Electrical Engineers (IEEE) Standard 81.If fall-of-potential tests cannot be performed, it is acceptable to measure resistance at each accessible ground rod using a clamp-on ground resistance tester. Provide the Engineer with written, certified test results for each testing location. | No Operator Requirement | Partial System OOS |  | 409 bldg ground cable
| 409 | Military service station | 409 Military service station | Lighting | Lighting-MSS |  | N/A | N/A | N/A | X | X | X | 9-1.8 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Lighting-MSS
| 409 | Military service station | 409 Military service station | Air Compressors | Air Compressor |  | Ingresoll-Rand | T-30 | N/A | X | X | 0 | Air Compressors | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Air compressor-MSS
| 409 | Military service station | 409 Military service station | Containment Systems | Service station containment |  | N/A | N/A | N/A | 0 | 0 | X | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | 409 containment
| 409 | Military service station | 409 Military service station | Containment Systems | Bollards-MSS-10 |  | N/A | N/A | N/A | 0 | 0 | X | General | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Bollards-MSS-10
| 5094 | Refueling Parking | 5094 Refueler Parking | Fuel Truck Containment Areas | 5094 Refueler parking yard |  | N/A | N/A | N/A | X | X | X | 11-1.1 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Refueler parking yard
| 5094 | Refueling Parking | 5094 Refueler Parking | Signage and Markings | Refueler parking yard-fencing |  | N/A | N/A | N/A | 0 | 0 | X | 2-7 | No Additional Manufacturer Requirements | No Operator/equipment Requirements | No Mission Impact |  | Refueler parking yard-fencing
Instructions:
1. Input all data as indicated on the sheet.
2. Additional documents referred to in the Special Considerations column shall be included as an appendix to this FMP.
3. The contractor shall generate a Component Unique Identifier (CUID) for each component utilizing the Component Acronym Sheet within this Work Book. The unique identifier must use the following:
Three letter Site Code - Facility # - Component Acronym - Sequential number
Example: AAD-00063A-RCVL-0001
If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment. Base Asset ID if used by site shall be cross referenced with CUID appropriately.
4. Utilize the UFC Section Reference Work Category as noted on the Component Acronym Sheet.
5. Enter any applicable manufacturer requirements not stated in the UFC. References are acceptable with attachments.
6. Enter any applicable operator support or government owned equipment required to complete the RM task.
7. Enter impact on system availability by performing the RM task. This could include shutdown, lockout, or similar impacts.
8. Enter contract information for any other contract, contractor, or government personnel performing the applicable task. This is applicable to other Centrally Managed Programs, SRM, MILCON, or Public Works/Civil Engineering projects.
9. Print Hard Copies as 11x17.

## FS-PF Schedule
FILTER SEPARATOR/PRE-FILTER MAINTENANCE SCHEDULES
Applicable Facility Assets | [10 empty] | Coalescer/Separator Information | [7 empty] | Special Considerations
Real Property Unique Identifier (RPUID) | Real Property Facility # | Real Property Facility Name | Operational Area | Component Type | Base Asset ID | Component Unique Identifier (CUID) | Make | Model | Capacity (GPM) | UFC Section Reference | Number of Coalescer Cartridges | Number of Separator Cartridges | Coalescer Cartridges Model # | Separator Cartridge Model # | Clean or Replace Separator Cartridge | Gasket Model # | Date Last Replaced | Replacement Due Date | Operator/Equipment Requirements | System Availability | Site Self Performs (Y/N) | Comments
| 109 | Fill stands | 109 Fillstands | Filter Separators | F/S 1 |  | Facet | HCS-643-236 | 600 GPM GPM/SCFM Gallons | 3-6.2 | 6 | 2 | CAA43-5SB/SS636FF-5 | CAA43-5SB/SS636FF-5 | Replace |  |  | 2024-03-03 |  |  | N | RMMR Contractor to Perform
| 109 | Fill stands | 109 Fillstands | Filter Separators | F/S 3 |  | Facet | HCS-643-236 | 600 GPM GPM/SCFM Gallons | 3-6.2 | 6 | 2 | CAA43-5SB/SS636FF-5 | CAA43-5SB/SS636FF-5 | Replace |  |  | 2024-03-03 |  |  | N | RMMR Contractor to Perform
| 109 | Fill stands | 109 Fillstands | Filter Separators | F/S 2 |  | Facet | HCS-643-236 | 600 GPM GPM/SCFM Gallons | 3-6.2 | 6 | 2 | CAA43-5SB/SS636FF-5 | CAA43-5SB/SS636FF-5 | Replace |  |  | 2024-03-03 |  |  | N | RMMR Contractor to Perform
Instructions:
1. Input all data as indicated on the sheet.
2. Additional documents referred to in the Special Considerations column shall be included as an appendix to this FMP.
3. The contractor shall generate a Component Unique Identifier (CUID) for each component utilizing the Component Acronym Sheet within this Work Book. The unique identifier must use the following:
Three letter Site Code - Facility # - Component Acronym - Sequential number
Example: AAD-00063A-RCVL-0001
If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment.
4. Utilize the UFC Section Reference Work Category as noted on the Component Acronym Sheet.
5. Enter any applicable manufacturer requirements not stated in the UFC. References are acceptable with attachments.
6. Enter any applicable operator support or government owned equipment required to complete the RM task.
7. Enter impact on system availability by performing the RM task. This could include shutdown, lockout, or similar impacts.
8. Filter Separators and Pre-Filters identified here shall also be provided in the Task Matrix Tab.
9. Print Hard Copies as 11x17.

## Component Acronym
Component Unique Identifier: | Site Code-Facility #-Component Acronym-Sequential #
Example: | AAD-00063A-RCVL-0001
NOTE: If component acronym is not listed, the contractor shall request an acronym be established through the HNC Project Manager and Project Engineer via email. Contractors may utilize other means of tracking/labeling assets such as QR codes in addition to the required CUID however, tracking/labeling must correlate with the CUID. This CUID shall be the standard for all DLA capitalized equipment
DLA Work Type Category | UFC Section Reference Work Category (Revised per Change 1, 29 April 2021) | Component Acronym
Air Compressors | Air Compressors | AIRC
Alarms | Externally Mounted Level Alarms (Section 8-9.9.1) | EMLA
| Internally Mounted Level Alarms (Section 8-9.9.3) | IMLA
Bollard | Bollards | BLRD
Building | Building HVAC | BHVAC
| Building Domestic Water System | BWTR
| Building Waste Water | BWSW
| Building - Lighting | BLTG
| Building - Architectural | BARCH
| Building - Fire Sprinkler System | BFIRE
Containment/Joints | Containment Systems (General) (Section 8-10.1) | CSGEN
| Concrete and Cement Brick Dike/Berm Walls (Section 8-10.2.1) | DKBW
| Dike/Berm Floors (Section 8-10.2.2) | DKBF
| Earthen Dike Walls (Section 8-10.3) | ETHDW
| Self-Diking or Vaulted Tank Containment (Section 8-10.4) | SDVTCS
| Flexible Membrane Liners (Section 8-10.5) | FXML
| Fuel Truck and Rail Car Containment Areas (Section 11-1.1) | FTKRCC
| Remote Spill Containment (Section 11-1.2) | RSCS
| Piers and Wharves Fuel Containment Systems (Section 5-1.2) - Testing | FPWCT
| Fuel Pier/Wharf Containment (PWS Section 3) | FPWC
Corrosion Control/Coatings | Aboveground Piping and Equipment Coatings (Section 6-10.1) | AGPCT
Miscellaneous | Miscellaneous Deactivated Components (Section 12-5) | MDEAC
Electrical/Lighting | Lighting (Section 9-1.8) | LIGHT
Electrical/Power | Electrical Equipment (Section 9-1.2) | ELEQ
| Power Cables (Section 9-1.3) | PWRCBL
| Motor Controls (Section 9-1.4) | MTRCT
| Panelboards (Section 9-1.5) | PNLB
| Electric Motors (Section 9-1.7) | ELEMT
| Electronic Equipment (9-1.9) | ELTREQ
| Card and Key Locks (Section 9-3) | CKLK
Electrical/Protection | Power Grounding Systems (Section 9-1.6.1) | PWRGS
| Static Grounding Systems (Section 9-1.6.2) | STGS
| Cathodic Protection (Section 9-2.1) | CP
| Lightning Surge Arresters (Section 9-2.2.1) | LSAR
| Lightning Protection Systems (Section 9-4) | LPTS
| Ground Verification System (Section 9-5) | GRVS
| Electronic Overfill Protection Systems (Section 9-6) | EOPS
Eyewash/Shower | Emergency Eyewash/Showers (Section 11-3) | EMEWSH
Fencing/ Gates | Fencing | FENC
| Gates | GATE
Filtration | Pre-Filters (Section 3-6.1) | PFVSL
| Filter Separators (Section 3-6.2) | FLSP
| Haypack Filters (Section 3-6.3) | HPKF
| Basket Strainers (Section 3-6.4) | BSTR
| Filter Separator Sump Heaters (Section 3-6.5) | FSSH
| Sidestream Filtration Systems (Section 8-9.11) | SSFTS
Fire Suppression Equipment | Flame Arrestors (Section 8-9.5) | FLMARR
| Foam Fire Protection Systems (Section 8-9.15) | FFPS
| Fire Protection Systems - Wet Pipe | FPRS
Fuel Laboratories | Ventilation Hoods (Section 11-4.1) | VENTHD
Gauges | Pressure and Pressure/Vacuum Gauges (Section 6-7.1) | PVGA
| Differential Pressure Gauges (Section 6-7.2) | DPGA
| Mechanical Tape Gauges (Section 8-9.7) | MTGA
| Mechanically Operated Tape Gauge (Section 8-9.8.1) | MOTGA
| Magnetostrictive Probes (Section 8-9.8.2) | MRPRB
| Servo Gauge (Section 8-9.8.3) | SRVGA
Generators | Back-Up Power Generators | BGEN
Heating Coils | Steam Type Heating Coils (Section 8-9.16.1) | STHC
| Thermal Fluid Type Heating Coils (Section 8-9.16.2) | TFTHC
| Electric Rod Type Heating (Section 8-9.16.3) | ERTH
Hoses | Loading Fuel Hoses (Section 3-9.1) | LDHS
| Offloading Fuel Hoses (Section 3-9.2) | OLHS
| Aircraft Fueling Hoses (Section 4-7.5) | ACFHS
Hydrazine | Hydrazine Charging Units (Section 10-3) | HDZCU
Inspections | Trouble Shoot | TRBST
| API 510 Inspections | API510
| API 653 or STI Inspection | API653
| Coatings Condition Survey | CCS
Issue/Receive - Ground | Dispenser Nozzles (Section 7-2) | DSNZ
| Dispenser Hoses (Section 7-3) | DSHS
| Breakaways (Section 7-4) | DSBW
| Swivels (Section 7-5) | DSSW
| Hose Retriever (Section 7-6) | HSRTV
| Dispenser Cabinet (Section 7-7) | DSCB
| Dispenser Meters (Section 7-8) | DSMTR
| Dispenser Filters (Section 7-9) | DSFLR
| Dispenser Strainers (Section 7-10) | DSSTR
| Ground Vehicle Fuel Piping (Section 7-11) | GVFP
| Emergency Shutoff Valves (Shear Valves) (Section 7-12) | ESHVL
| Dispenser Sumps (Section 7-13) | DSSMP
| Transition Sumps (Section 7-14) | TRSMP
| Remote Dispenser Pumps (Section 7-15.1) | RDSP
| Self-Contained Dispenser Pumps (Section 7-15.2) | SCDSP
| EFSO Systems (Section 7-16) | EFSO
| Stage I Vapor Recovery (Section 7-17.1) | SIVP
| Stage II Vapor Recovery (Section 7-17.2) | SIIVP
| Vapor Burners (Section 7-17.3) | VPBNR
| Point Sensor - Dry (Section 7-19.1.1) | PSDRY
| Automatic Line Leak Detector (Section 7-19.1.2) | ALLD
| Visual Monitoring (Section 7-20.1) | VSLM
Issue/Receive - Marine | Marine Receipt (Section 5-2) | MRNRCP
| Marine Issue (Section 5-3) | MRNISU
| Marine Loading Arms (Section 5-4) | MRNLA
| Marine Transfer Hoses (Section 5-5.1) | MBTHS
| Underwater Hoses (Section 5-5.2) | UWHS
| Single Point Mooring Systems (Section 5-7.1) | SPMSS
| Multi Point Mooring Systems (Section 5-7.2) | MPMSS
| Submerged Piping Systems (Section 5-8) | SMPS
| Boom Reels (Section 5-9) | BMRL
Liquefied Petroleum | Liquefied Petroleum Tanks (Section 10-1.1) | LPTANK
| Liquefied Petroleum Pipelines (Section 10-1.2) | LPPIPE
| Liquefied Petroleum Vapor Lines (Section 10-1.3) | LPVPL
| LPG Vaporizers (Section 10-1.4) | LPGVPZ
| Petroleum Gas Regulators (Section 10-1.5) | PGREG
| Liquefied Petroleum Gas Hoses (Section 10-1.6) | LPGHS
Meter/ calibrations | Positive Displacement Meters (Section 3-7.1) | PDMT
| Turbine Flow Meters (Section 3-7.2) | TBFMT
| Orifice Flow Meters (Section 3-7.3) | OFMT
Natural Disaster | Natural Disaster
Natural Gas | CNG Piping (Section 10-2.1) | NGPIPE
| CNG Compressors (Section 10-2.2) | NGCOMP
| CNG Storage (Section 10-2.3) | NGSTOR
| CNG Dispensers (Section 10-2.4) | NGDS
| CNG Dispenser Hoses (Section 10-2.5) | NGDSHS
Nozzle | Hydrant Adapters (Section 4-7.2) | HADP
| Fueling Nozzles (Section 4-7.3) | FLNZ
Other | Fuel Additive Injectors (Section 3-11) | FAIJ
Pantograph | Fixed Pantographs (Section 4-7.1.1) | FXPNT
| Detachable Pantographs (Section 4-7.1.2) | DTPNT
Piping | On-Base Pipelines (Section 6-1.1) | OBPL
| Non-DOT Regulated (Section 6-1.2.1) | NDPL
| Aboveground Piping (Section 6-1.3) | AGPL
| Double-Wall Piping (Section 6-1.4) | DWPL
| Low Point Drains (Section 6-12.1) | LPDN
| High Point Vents (Section 6-12.2) | HPVT
| Sight Flow Indicators (Section 6-12.3) | SFND
| Rope Sensor Systems (Section 6-13.1.1) | RPSS
| Point Sensor - Dry (Section 6-13.1.2) | PSDRY
| Visual Monitoring (Section 6-14.1) | VSLM
| Pipe Penetrations (Section 8-10.6) | PPEN
| Deactivated Petroleum Fuel Pipelines (Section 12-3) | DEACPL
Pressure/Temperature Control | Air Eliminator Tanks (Section 3-10.1) | AELT
| Automatic Air Vents (Section 3-10.2) | AAVT
| Surge Suppressors (Section 4-7.4) | SRGSP
| Thermal and Pressure Relief Valves (Section 6-6.3) | TPRVL
| Pressure Transmitters (Section 6-7.3) | PRTR
| Differential Pressure Transmitters (Section 6-7.4) | DPTR
| Flexible Ball Joints (Section 6-8) | FBLJT
| Dial Thermometer (Section 6-9.1) | DTHMR
| Emergency Vents (Section 8-9.4) | EMGVT
Pump | Centrifugal Pumps (Section 3-8.1) | CENP
| Vertical Inline Pumps (Section 3-8.2) | VILP
| Vertical Turbine/Submerged Turbine Pumps (Section 3-8.3) | VTSP
| Sliding Vane Pumps (Section 3-8.5) | SLVP
| Gear Pumps (Section 3-8.6) | GERP
| Diaphragm Pumps (Section 3-8.7) | DIAP
| Internal Combustion Drives (Section 3-8.8) | ICDR
| Gearboxes (Section 3-8.9) | GRBX
| Deactivated Petroleum Fuel Pumps (Section 12-4) | DEACP
Signage/Markings | Signage and Markings (Section 2-7) | SIGN
Structures | Pumphouse/Filter Buildings (Section 11-2.1) | PFBLDG
| Canopies (Section 11-2.2) | CNPY
| Cranes and Hoists (Section 11-6) | CRNHST
Tank | Aboveground Field-Erected Tanks (Section 8-4) | AGFET
| Geodesic Dome Roofs (Section 8-4.2) | GEODR
| Foundations (Section 8-4.3) | FOUND
| Aboveground Shop Fabricated Tanks (Section 8-5.1) | AGSFP
| Self-Diking or Vaulted Tanks (Section 8-5.2) | SDVT
| Rectangular Concrete-Encased Tanks (Section 8-5.3) | RCET
| Single-Walled Underground Shop-Fabricated Tanks (Section 8-5.4.1) | UGSSFT
| Double-Walled Underground Shop-Fabricated Tanks (Section 8-5.4.2) | UGDSFT
| Underground Field-Constructed Tanks (Cut and Cover Tanks) (Section 8-6) | UGFET
| Tank Cleaning (Section 8-7) | TCLEAN
| Aluminum Honeycomb Floating Pans (Section 8-9.1.1) | AHFP
| Steel Floating Pans (Section 8-9.1.2) | STLFP
| Pontoon Floating Pans (Section 8-9.1.3) | PTNFP
| Floating Roofs (Section 8-9.1.4) | FLTRF
| Floating Roof and Pan Pressure/Vacuum Vents (Section 8-9.1.5) | FPPVV
| Floating Roof and Pan Legs (Section 8-9.1.6) | FRPLG
| Secondary Tank Bottoms (Section 8-9.2) | SNDTB
| Tank Pressure/Vacuum Vents (Section 8-9.3) | TPVVT
| Product Saver Tanks (Section 8-9.10) | PRDST
| Fill Ports (Section 8-9.12) | FPRT
| Point Sensor - Dry (Section 8-9.13.1) | PSDRY
| Point Sensor - Wet (Section 8-9.13.2) | PSWET
| Point Sensor - Pressure/Vacuum (Section 8-9.13.3) | PSPV
| Visual Leak Detection (Section 8-9.13.4) | VSLLD
| Floating Suction Lines (Section 8-9.14) | FLTSL
| Stilling Wells (Section 8-9.17) | STGW
| Deactivated Petroleum Fuel Tanks (Section 12-2) | DEACT
Testing | Pressure Testing
Underground Pits | Isolation Valve Pits (Section 6-11.1) | ISVLP
| Hydrant Fuel Pits (Section 6-11.2) | HDFP
| High Point Vent Pits (Section 6-11.3) | HPVP
| Low Point Drain Pits (Section 6-11.4) | LPDP
| Lateral Control Pits (Section 6-11.5) | LTCP
Valves | General System Control Valves (Section 4-3.2.1) | GSCVL
| Refuel Control Valves (Section 4-3.2.5) | RCVL
| Pressure Relief Valves (Section 4-3.2.6) | PRCVL
| Defuel Control Valve (Section 4-3.2.7) | DFCVL
| Dual Rate-of-Flow Control Valves (Section 4-3.2.8) | DRFCVL
| Combination Dual Rate-of-Flow Control and Solenoid Valves (Section 4-3.3.1) | CFSCVL
| Dual Pressure Relief, Solenoid Shutoff, and Check Valves (Section 4-3.3.2) | DPSCVL
| Non-Surge Check Valves (Section 4-4.2.1) | NSCKVL
| Filter Separator Control Valves (Section 4-4.2.2) | FSCVL
| Defuel/Flush Valves (Section 4-4.2.3) | DFFCVL
| Issue Venturi (Section 4-4.2.4) | ISVTR
| Return Venturi (Section 4-4.2.5) | RTVTR
| Back Pressure Control Valves (Section 4-4.2.6) | BPCVL
| Pressure Control Valves (Section 4-4.2.7) | PCVL
| Hydrant Control Valves (Section 4-4.2.8) | HCVL
| Emergency Shut-off Valves (Section 4-4.2.9) | ESOVL
| Pantograph Control Valves (Section 4-5.2.12) | PTCVL
| Pantograph Pressure Control Valves (Section 4-5.2.13) | PTPCVL
| Overfill Valve for Product Recovery Tanks (Section 4-8.1) | OVLPRT
| Plug Valves - Lubricated (Section 6-6.2.1) | PLVL
| Plug Valves - Non-lubricated (Section 6-6.2.2) | NPLVL
| Gate Valves (Section 6-6.2.3) | GTVL
| Ball Valves (Section 6-6.2.4) | BLVL
| Double Block and Bleed Valves (Section 6-6.2.5) | DBBVL
| Butterfly Valves (Section 6-6.2.6) | BFVL
| Globe Valves (Section 6-6.2.7) | GLVL
| Check Valves (Section 6-6.2.8) | CKVL
| Line Blanks, Ring Spacers, and Spectacle Blinds (Section 6-6.2.9) | BLIND
| Manual Valve Gear Operators (Section 6-6.2.10) | MVLGO
| Fire Valves (Section 6-6.4.1) | FRVL
| Fusible Link Butterfly Valves (Section 6-6.4.2) | FLBFVL
| Truck Fill Valves (Section 6-6.5.1) | TFVL
| Motor Operators (Section 6-6.6) | MTROP
| External High Level Shutoff Valves (HLSO) (Section 8-9.6.1) | EHLSVL
| Internal HLSO Valves (Section 8-9.6.2) | IHLSVL
Waste | Oil/Water Separators (Section 11-5) | OWS

## Versions and Notes
Version | Date | Description of changes
v2.0 | 2021-08-18 | Updated Task Matrix to meet UFC 3-460-03 Change 1 , 29 April 2021
Updated Component Acronym Tab to meet UFC 3-460-03 Change 1 , 29 April 2021
v2.1 | 2022-04-20 | Task Matrix Tab - Deleted all services facility # columns and combined into one. Renamed "Real Property Facility #"
Task Matrix Tab - Added "RPUID" to Real Property Unique Identifier column
Task Matrix Tab - Added "Real Property" to Facility Name
Task Matrix Tab - Added column for "Base Asset ID"
Task Matrix Tab - Added "Additional" and "RM" to Manufacturer Requirements
Task Matrix Tab - Changed Comment note for Filter Separator
Task Matrix Tab - Changed Note #3 To add "Base Asset ID if used by site shall be cross referenced with CUID appropriately."
Task Matrix Tab - Changed note #7 under instructions for Task Matrix to clarify this column
Task Matrix Tab - Changed note #8 under instructions for Task Matrix to clarify this column
Added new tab for RM schedule to be included
Added new Tab for Filter Separator/Pre-Filter Schedule with instructions
Administrative Tab - changed Installation to Site and added Site Code to comply with new requirements as the three letter DLA site code is obsolete
General Facility Description - Changed the Instructions
Reversed columns 'Base Asset ID' and 'CUID' to match RM report for all tabs
Added FMP version to footer
v2.2 | 2022-10-31 | Administrative Tab - Added rows for POC Name for all
Administrative Tab - Added RPSUID in cell B2
General Facility Description Tab - Added "fuel type"
Communication Plan Tab - added "coordination for access"
Safety Tab - Changed instructions to read "Site Specific Addendum and Activity Hazard Analysis, which are Attachments to the APP, specific to activities or tasks related to recurring maintenance for this site."
Changed footer for tabs to FMP v2.2
Task Matrix and FS/PF Schedule added not to print as 11x17. Also changed in page layout.