## C4
PM Procedures, Instructions, and Trades in Archibus
PM Procedure | Instructions | Primary Trade
COMS-CUP-001S | 1. Stop and start fan with local switch. 2. Check motor and fan shaft bearings for noise, vibration. 3. Lubricate bearings. 4. Check belts for wear, tension and alignment, if applicable. 5. Adjust belts or replace as required. 6. Inspect VFD enclosure and clean, if applicable. 7. Check blower intake dampers, lubricate; if applicable. 8. Check electrical wiring and connections: tighten loose connections. 9. Clean fan and surrounding area. 10. Complete work order data | COMS_CUP OPER
COMS-CUP-002A | **Annual PM must be completed in conjunction with Quarterly and Monthly PMs** 1. Clean combustion chamber, check for air or gas leaks. 2. Inspect and clean burner, blower, electrodes, cad cell, chimney base and smoke pipe. 3. Inspect fuel system for leaks and change fuel filter element, if applicable. 4. Operate and check electrical wiring and connections. 5. Inspect boiler tubes for scale and leakage; replace if any visible defects. 6. Clean Firebox 7. Perform burner efficiency test. 8. Clean or replace nozzle, strainers, gas jets/orifices. 9. Replace fuel filter. 10. Check all safety controls. 11. Complete work order data. | COMS_CUP OPER
COMS-CUP-002M | 1. Inspect fuel lines and connections for damage, if applicable. 2. Check main flame failure protection and flame detection scanners, if applicable. 3. Check operation of control switches including hot water temperature limit and combustion air proving. 4. Check condition of safety relief valve. 5. Check operation of boiler low water cut off devices. 6. Check indicator lights, sight glasses and pressure gauges. 7. Clean area around boiler. 8. Complete work order data | COMS_CUP OPER
COMS-CUP-002Q | **Quarterly PM must be completed in conjunction with Monthly PM** 1. Check for proper operational response of burner to controls. 2. Check and lubricate burner, blowers and motors as required. 3. Check draft diverter and clear openings if clogged. 4. Check safety and limit controls. 5. Clean area around the equipment. 6. Complete work order data. | COMS_CUP OPER
COMS-CUP-003Q | 1. Check with operating personnel for deficiences. 2. Run microprocessor check, if applicable. 3. Check controls and unit for proper operation. 4. Check for unusual noise or vibration. 5. Replace air filters. 6. Lubricate shaft and motor bearings. 7. Check belts for wear, proper tension, and alignment; adjust as necessary. 8. Check humidifier, if applicable. 9. Check humidity lamp or canister, if applicable; replace if necessary. 10. Inspect exterior piping and valves for leaks. 11. Tighten connections as required. 12. Clean area around unit. 13. Complete work order data | COMS_CUP OPER
COMS-CUP-003S | **Semi-Annual PM must be completed in conjunction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan blower, motor and drain piping as required. 3. Clean humidifier pan, if applicable. 4. Check operation of unit. 5. Check refrigerant pressure, if applicable; add refrigerant as required. 6. Clean area around unit. 7. Add biocide. 8. Complete work order data. | COMS_CUP OPER
COMS-CUP-004S | 1. Check with operating personnel for deficiencies. 2. Clean pump exterior and check for corrosion on pump exterior. 3. Check for leaks on suction and discharge piping. 4. Check pump and motor operation for vibration and noise. 5. Inspect VFD enclosure and clean, if applicable. 6. Check motor and pump alignment, if applicable and adjust as necessary. 7. Lubricate pump and motor as required. 8. Check pressure gauge readings and flow rates if available. 9. Clean area around pump. 10. Complete work order data | COMS_CUP OPER
COMS-CUP-005A | 1. Check with operating personnel for deficiencies. 2. Inspect, clean and adjust control valves and thermostat. 3. Inspect coils, connections and piping for leaks. 4. Check fan and motor for vibration and noise. 5. Check electrical wiring to motor. 6. Change air filter(s). 7. Check unit heater operation. 8. Clean area around the heater. 9. Complete work order data | COMS_CUP OPER
COMS-CUP-006S | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check electrical wiring and connections. 6. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 7. Clean drain pan and blower as required. 8. Perform operational check of unit. 9. Check refrigerant pressure. 10. Add or remove refrigerant, as required. 11. Clean or replace air filter, as applicable. 12. Clean area around unit. 13. Complete work order data | COMS_CUP OPER
COMS-CUP-006S | 1. Check with operating or area personnel for deficiencies. 2. Check temperature gauges for proper operating temperatures. 3. Check steam modulating valve and steam condensation trap for proper operation, if applicable. 4. Inspect heat exchanger and adjacent piping for torn or deteriorated insulation. 5. Clean area around the heat exchanger. 6. Complete work order data | COMS_CUP OPER
COMS-CUP-007A | **Annual PM must be completed in conjuction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan and condensate drain as required. 3. Clean blower and motor as required. 4. Check electrical connections. 5. Inspect VFD enclosure and clean, if applicable. 6. Check operation and clean dampers, louvers and shutters; lubricate as required. 7. Check filters, replace if needed. 8. Check belts, replace or adjust as needed, where applicable. 9. Apply biocide. 10. Complete work order data. | COMS_CUP OPER
COMS-CUP-007Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. Adjust or replace belts as required. 6. Inspect exterior piping and valves for leaks. Inspect coils for debris. 7. Check refrigerant pressure. Add or remove refrigerant, as required. 8. Tighten connections as required. 9. Replace air filters. 10. Cycle Drum Pre-Filters 11. Clean area around unit. 12. Complete work order data | COMS_CUP OPER
COMS-CUP-008S | 1. Check with operating or area personnel for deficiencies. 2. Check operation of unit for water leaks, noise and vibration. 3. Clean and inspect hot water basin. 4. Check electrical wiring and connections and adjust as reuired. 5. Lubricate motor and fan bearings. 6. Check fan blades or blower for imbalance and tip clearance. 7. Check belts for wear, tensiona dn alignment; adjust as required. 8. Drain and flush cold water sump and clean strainer. 9. Brush clean inside of tower and remove scale build-up with appropriate compound, as required. 10. Refill with water and check make-uppiping for leakage; repair as required. 11. Inspect and clean around cooling tower. 12. Condition assessment of structure (enter into Craftsperson's notes) 13. Complete work order data. | COMS_CUP OPER
COMS-CUP-009A | **Annual PM must be completed in conjuction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan and condensate drain as required. 3. Clean blower and motor as required. 4. Check electrical connections. 5. Inspect VFD enclosure and clean, if applicable. 6. Check operation and clean dampers, louvers and shutters; lubricate as required. 7. Check filters, replace if needed. 8. Check belts, replace or adjust as needed, where applicable. 9. Apply biocide. 10. Complete work order data. | COMS_CUP OPER
COMS-CUP-009Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. Adjust or replace belts as required. 6. Inspect exterior piping and valves for leaks. Inspect coils for debris. 7. Check refrigerant pressure. Add or remove refrigerant, as required. 8. Tighten connections as required. 9. Replace MERV-13 Filter, where applicable. 10. Clean area around unit. 11. Complete work order data | COMS_CUP OPER
COMS-CUP-012S | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks. 8. Tighten connections as required. 9. Replace air filters, if applicable. 10. Clean area around unit. 11. Put Biocide into evaporator pan. 12. Clean area around the equipment. 13. Complete work order data. | COMS_CUP OPER
COMS-CUP-016S | 1. Check with pump operating personnel for any obvious deficiencies. 2. Obtain and put on safety equipment for working with chemicals: goggles, apron, gloves and respirator. 3. Check oil level in pump with dipstick; add oil as necessary. 4. Inspect belt condition and tension on pump; adjust as required. 5. Flush slurry pump with fresh water. 6. Pressure test pump. 7. Inspect pump motor. 8. Operate pump and check for leaks, excessive noise and vibration. 9. Clean area around the equipment. 10. Complete work order data. | COMS_CUP OPER
COMS-CUP-026A | 1. Check baseboard during operating season. 2. Check hot water piping and control valves for leaks. 3. Inspect condition of radiant heat fins, issue work orders to correct as necessary. 3. Check electric baseboard electrical connections. 4. Check controls for proper operation. 5. Clean area around the equipment. 6. Complete work order data. | COMS_CUP OPER
COMS-CUP-050S | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks. 8. Tighten connections as required. 9. Replace air filters. 10. Clean coil(s). 11. Clean blower and motor as required. 12. Check electrical connections. 13. Clean area around unit. 14. Complete work order data. | COMS_CUP OPER
COMS-CUP-100A | **Note: Annual PM must be performed in conjunction with Monthly PM** 1. Check and tighten electrical connections. 2. Verify proper calibration of all safety controls. 3. Megohm motor windings and record readings. 4. Replace oil filter and oil return filter/driers. Add oil as necessary. 5. Inspect oil filter thoroughly for any aluminum particles indicating bearing wear. 6. Clean or backflush heat exchanger. 7. Replace starter coolant. 8. Clean inside of VFD enclosure. 9. Perform oil analysis on compressor lube oil. 10. Perform refrigeration anaylsis. 11. Perform vibration analysis. 12. Clean condenser and evaporator tubes with soft bristle bronze or nylon brush. Do NOT use steel bristle brush. 13. Lubricate motor based on motor manufacturer's recommendations. 14. Inspect vent piping and safety relief valves. 15. Clean area around the equipment. 16. Complete work order data. | COMS_CUP OPER
COMS-CUP-100M | 1. Check with operating personnel for deficiencies. 2. Check unit for proper operation. 3. Check oil level, add oil as required. 4. Check oil temperature and record. 5. Check oil return system operation 6. Check motor starter operation. 7. Check compressor for excessive noise and vibration. 8. Check sump heater and thermostat operation (chiller must be shutdown). 9. Check 3-phase voltage and current balance. 10. Verify proper operation/setting of safety controls. 11. Verify condenser and evaporator water flows. 12. Leak check and repair as needed. 13. Check motor mounting screws to ensure tightness. 14. Clean area around the equipment. 15. Complete work order data. | COMS_CUP OPER
COMS-CUP-100O | **Note: PM must be performed in conjunction with Annual & Monthly PM** 1. Notify the COR in writing thirty (30) calendar days before testing will be performed. **Government Inspector MUST BE PRESENT during testing unless written waiver is provided by COR** 2. Peform Eddy current testing and inspect evaporator and condenser tube bundles. 3. Provide report of test results to COR within seven (7) calendar days of testing. 4. Clean area around the equipment. 5. Complete work order data. | COMS_CUP OPER
COMS-CUP-100O2 | **Note: PM must be performed in conjunction with Annual & Monthly PM** 1. Change compressor oil. | COMS_CUP OPER
COMS-CUP-701A | **Note-Annual PM must be performed in conjunction with monthly PM** 1. Check with operating personal for deficiencies. 2. Run service test to check unit for proper operation. 3. Inspect and clean cooler tubes as necessary. Inspect the entering and leaving thermistors for signs of corrosion or scale. Replace the sensor if corroded or remove any scale if found. 4. Inspect and clean condenser tubes as necessary. Inspect the entering and leaving thermistors for signs of corrosion or scale. Replace the sensor if corroded or remove any scale if found. 5. Remove and replace internal compressor oil filter. 6. Remove and replace external compressor oil filter. 7. Check all electrical connections. Tighten as necessary. 8. Check accuracy of all transducers for each circuit, record readings, replace as necessary. 9. Check accuracy of thermistors, record readings, replace if greater than ± 2°F (1.2°C) variance from calibrated thermometer. 10. Obtain and test an oil sample, record results, change as necessary. 11. Check to be sure that the proper amount of inhibitor is present in the chilled water loop, record readings. 12. Check all refrigerant strainers and filter driers for pressure drops, record readings, replace or clean as necessary. 13. Clean chilled water strainers. 14. Check condenser water regulating valve operation, if equipped. 15. Clean condenser water strainers. 16. Clean area around the equipment. 17. Complete work order data. | COMS_CUP OPER
COMS-CUP-701M | 1. Check with operating personal for deficiencies 2. Run service test to check unit for proper operation. 3. Check moisture indicating sight glass for possible refrigerant loss and presence of moisture. 4. Ensure compressor mounting hardware to ensure tightness. 5. Ensure equipment and surrounding area is free from fluids and debris. 6.Clean area around the equipment. 7. Complete work order data. | COMS_CUP OPER
COMS-CUP-701Q | **Note-Quarterly PM must be performed in conjunction with monthly PM** 1. Check all refrigerant joints and valves for refrigerant leaks, repair as necessary. 2. Check oil filter pressure drops, replace as necessary. 3. Check chilled water flow switch operation. 4. Clean area around the equipment. 5. Complete work order data. | COMS_CUP OPER
COMS-EAS-001A | 1.Verify reader operation with valid badge. 2.Inspect for damage or equipment deterioration. 3.Verify electronic locking device and power supplies are in working order. 4.Tighten loose hardware 5.Lubricate locking devices and notate date. 6. Document all completed work on PM work request. | COMS_ELECTRONICS
COMS-EAS-001Q | 1. Verify reader operation with valid and void badge. 2. Inspect for damage or equipment deterioration. 3. Verify electronic locking device and power supplies are in working order. 4. Tighten loose hardware. 5. Lubricate locking devices. 6. Complete work order data. | COMS_ELECTRONICS
COMS-EAS-002Q | 1. Check camera-viewing quality. 2. Operate all automated camera's PTZ controls. 3. Check camera mounts and enclosures for component deterioration. Replace corroded components with corrosion resistant hardware. 4. Clean camera housing, lens and viewing glass. 5. Replace desiccant pack. 6. Complete work order data. | COMS_ELECTRONICS
COMS-EAS-002S | 1. Check camera-viewing quality. 2.Operate all automated camera's PTZ controls. 3.Check camera mounts and enclosures for component deterioration. Replace corroded components with corrosion resistant hardware. 4.Clean camera housing, lens and viewing glass. 5.Verify automated camera's preset programming. 6.Complete work order data. | COMS_ELECTRONICS
COMS-EAS-003Q | 1. Check speakerphone operation. 2.Check speaker voice quality. 3.Check for tone disconnect. 4.Complete work order data. | COMS_ELECTRONICS
COMS-EAS-004Q | 1. Verify all DVR's, monitors, keyboard controllers and fiber optic transceivers are in working order. 2. Verify remote switching system activates gates and doors. 3. Verify automated camera's preset programming. 4. Check all keyboard controllers at remote locations. 5. Clean equipment and surrounding area. 6. Complete work order data. | COMS_ELECTRONICS
COMS-ELEC-002A | 1. Examine the exterior of the transformer for any damage, cracks, rust or leaks; check around bushings, gaskets and pressure relief device . 2. Remove the covers or open the doors. 3. Check for signs of moisture or overheating. 4. Check for voltage creeping over insulated surfaces, such as evidenced by cracking or carbonization. 5. Check fans, motors and other auxiliary devices for proper operation; where applicable. 6. Check the condition of the ground system. 7. Clean transformer and the surrounding area. 8. Replace the covers or close the doors. 9. Complete work order data. | COMS_ELEC
COMS-ELEC-002B | 1. Examine the exterior of the transformer for any damage, cracks, rust or leaks; check around bushings, gaskets and pressure relief device . 2. Remove the covers or open the doors. 3. Check for signs of moisture or overheating. 4. Check for voltage creeping over insulated surfaces, such as evidenced by cracking or carbonization. 5. Check fans, motors and other auxiliary devices for proper operation; where applicable. 6. Check the condition of the ground system. 7. Clean transformer and the surrounding area. 8. Replace the covers or close the doors. 9. Complete work order data. | COMS_ELEC
COMS-ELEC-003A | 1. Examine the exterior of the transformer for any damage, cracks, rust or leaks; check around bushings, gaskets and pressure relief device. 2. Remove the covers or open the doors. 3. Check for signs of moisture or overheating. 4. Check for voltage creeping over insulated surfaces, such as evidenced by cracking or carbonization. 5. Check the condition of the ground system. 6. Check and record the oil level, pressure and temperature readings. 7. Check fans, motors and other auxiliary devices for proper operation; where applicable. 8. Clean transformer exterior and the surrounding area. 9. Replace the covers or close the doors. 10. Complete work order data. | COMS_ELEC
COMS-ELEC-004A | 1. Check with operating or area personnel for deficiencies. 2. Inspect wiring, wiring connections, and fuse blocks for looseness, charring, evidence of short circuiting, overheating and tighten all connections. 3. Inspect general condition of transfer switch and clean exterior and surrounding area. 4. Perform complete operational testing. 5. Clean area around the equipment. 6. Complete work order data. | COMS_ELEC
COMS-ELEC-005A | 1. Examine the exterior of the switch for any damage. 2. Check the condition of the ground system. 3. Clean the exterior of the switch and operating mechanism. 4. Clean the area around the switch. 5. Complete work order data | COMS_ELEC
COMS-ELEC-006Q | 1. Check with operating or area personnel for deficiencies. 2. Check starter lights, replace if required. 3. Check for excessive heat, odors, noise, and vibration. 4. Clean motor control center exterior and surrounding area. 5. Complete work order data. | COMS_ELEC
COMS-ELEC-007A | 1. Contractor must make every effort to schedule outage to perform this mainteance. 2. Check with operating or area personnel for deficiencies. 3. Check for proper tightness of electrical connections and circuit breaker seating. 4. Check circuit breakers, conductors, wires for signs of overheating. 5. Check any connected surge protective devices or other ancilliary devices. 6. Clean and check general condition of panel. 7. When operationally safe to do so each circuit breaker must be opened/closed two times. 8. Perform a thermographic inspection. 9. Clean area around the equipment. 10. Complete work order data. | COMS_ELEC
COMS-ELEC-007B | 1. Contractor must make every effort to schedule outage to perform this mainteance. 2. Check with operating or area personnel for deficiencies. 3. Check for proper tightness of electrical connections and circuit breaker seating. 4. Check circuit breakers, conductors, wires for signs of overheating. 5. Check any connected surge protective devices or other ancilliary devices. 6. Clean and check general condition of panel. 7. When operationally safe to do so each circuit breaker must be opened/closed two times. 8. Perform a thermographic inspection. 9. Clean area around the equipment. 10. Complete work order data. | COMS_ELEC
COMS-ELEC-008A | 1. Check with the operating or area personnel for any obvious deficiencies. 2. Check oil level; add oil as required. 3. Change oil and oil filter; check transmission oil level. 4. Check that the crankcase heater is operating properly. 5. Replace air filter. 6. Check wiring, connections, switches, etc.; adjust as required. 7. Check starter for proper operation; lubricate as necessary. 8. Check fuel nozzles, fuel regulator and ignition device condition; service or replace as required. 9. Perform 30 minute generator test run; check for proper operation. 10. Check and record transmission oil pressure and temperature, and natural gas pressure. 11. Record running time: beginning hours; ending hours. 12. Check that the charger is operating properly. 13. Check for any signs of corrosion on battery terminals or wires. 14. Check the electrolyte level in the batteries; add if required. 15. Check the specific gravity of the electrolyte in a 10% sample of the batteries. 16. Check 25% of terminal-to-cell connection resistance; rehabilitate connections as required; add anti-corrosion grease to battery terminals and connections. 17. Measure and record individual cell and string float voltages. 18. Clean area around generator. 19. Complete work order data. | COMS_ELEC
COMS-ELEC-008M | 1. Check with the operating or area personnel for any obvious deficiencies. 2. Check oil level; add oil as required. 3. Check that the crankcase heater is operating properly. 4. Check starter for proper operation; lubricate as necessary. 5. Perform 30 minute generator test run; check for proper operation. 6. Check that the charger is operating properly. 7. Check for any signs of corrosion on battery terminals or wires. 8. Check the electrolyte level in the batteries; add if required. 9. Clean area around generator. 10. Complete work order data. | COMS_ELEC
COMS-ELEC-010M | 1. Check that the charger is operating properly. 2. Check for any signs of corrosion on the battery terminals or wires. 3. Check the electrolyte level in the batteries; add if required. 4. Check the specific gravity of the electrolyte in a 10% sample of the batteries, if applicable. 5. Clean area around batteries. 6. Complete work order data. | COMS_ELEC
COMS-ELEC-010Q | **Note: Perform in conjunction with monthly PM. 1. Check 25% of terminal-to-cell connection resistance; rehabilitate connections as required; add anti-corrosion grease to battery terminals and connections. 2. Measure and record indi\vidual cell and string float voltages. 3. Clean area around the equipment. 4. Complete work order data. | COMS_ELEC
COMS-ELEC-011S | 1. Test for proper operation, replace lamps as required. 2. Clean exterior of cabinet and light heads. 3. Check wiring for obvious defects. 4. Adjust lamp heads for maximum illumination of area. 5. Clean area around the equipment. 6. Complete work order data. | COMS_ELEC
COMS-ELEC-012S | 1. Check that the charger is operating properly. 2. Check for any signs of corrosion on the battery terminals or wires. 3. Check the electrolyte level in the batteries; add if required. 4. Check the specific gravity of the electrolyte in a 10% sample of the batteries. 5. Check 25% of terminal-to-cell connection resistance; rehabilitate connections as required; add anti-corrosion grease to battery terminals and connections. 6. Measure and record individual cell and string float voltages. 7. Clean area around batteries. 8. Complete work order data. | COMS_ELEC
COMS-ELEC-014A | 1. Remove the covers. 2. Check for signs of moisture or overheating. 3. Check condition of the ground system. 4. Replace the cover. 5. Check bolts for tightness. 6. Clean the surrounding area. 7. Complete work order data. | COMS_ELEC
COMS-ELEC-015A | 1. Check with operating or area personnel for deficiencies. 2. Remove switchboard from service, coordinate with appropriate authority. 3. Remove covers. 4. Clean interior. 5. Complete inspection tasks and maintenance items indicated in the Electrical Switchgear and Switchboard Assemblies Report. 6. Check the records on the circuit breaker for any full current rated trips which may indicate a potential problem. 7. Examine the exterior of the switchboard for any damage or moisture. 8. Check operation of circuit breaker tripping mechanism and relays. 9. Check the operation of the circuit breaker charging motor. 10. Install covers. 11. If applicable, check all interlocks for proper operation. 12. Operate the switching handle and check the locking mechanism. 13. Clean switchboard exterior and the surrounding area. 14. Place switchboard back in service, notify appropriate authority. 15. Attach electronic copy of report to PM work request record in FMMS. 16. Complete work order data and inspection form. | COMS_ELEC-LINE
COMS-ELEC-015M | 1. Clean surrounding area. 2. Check indicating lamps and meters for proper operation; replace burnt lamps. 3. Complete work order data. | COMS_ELEC-LINE
COMS-ELEC-020A | 1. Clean exterior of unit. 2. Check, notate expiration date and replace if expired. 3. Complete work order data. 4. NOTATE EXPIRATION DATE ON WORK REQUEST | COMS_ELEC
COMS-ELEC-023O | 1. All inspections and maintenance shall be as per Inspection/Maintenance Repair of Electrical Distribution System Form. 2. Inspect wood pole and crossarms. 3. Inspect insulators and bushings and lightning arrestors. 4. Inspect guys and anchors. 5. Inspect the conductors and ground wires. 6. Inspect hardware, switches, fuses and connections. 7. Maintain wood poles and crossarms as per checklist. 8. Clean area around the equipment. 9. Complete work order data and Inspection/Maintenance Repair of Electrical Distribution System Form. | COMS_ELEC-LINE
COMS-ELEC-024B | 1. Check that all ground and line connections are tight, short and direct and repair as needed. 2. Clean surrounding area from debris or other conductive materials. 3. Complete work order data. | COMS_ELEC
COMS-ELEC-025A | 1. Assure proper safety guidelines prior to deenergizing equipment. 2. Disconnect from power supply prior to cleaning. 3.Clean with mild detergent to maintain light visibility. 4.Thoroughly dry dome and lenses prior to reassembly. 5. Reconnect power and check operation. 6. Complete work order data. | COMS_ELEC
COMS-ELEC-050A | 1. Check with operating or area personnel for deficiencies. 2. Inspect wiring, wiring connections, and fuse blocks for looseness, charring, evidence of short circuiting, overheating. 3. Inspect general condition of equipment and clean exterior and surrounding area. 4. Perform complete operational testing. 5. Complete work order data. | COMS_ELEC
COMS-ELEC-051A | 1. Check with operating or area personnel for deficiencies. 2. Inspect wiring, wiring connections, and fuse blocks for looseness, charring, evidence of short circuiting, overheating. 3. Replace filters. 4. Perform complete operational testing. 5. Clean area around the equipment. 6. Complete work order data. | COMS_ELEC
COMS-ELEC-051Q | 1. Check with operating or area personnel for deficiencies. 2. Inspect general condition of equipment and clean exterior and surrounding area. 3. Clean filters. 4. Complete work order data. | COMS_ELEC
COMS-ELEC-100A | 1. Consult manufacturers' operation and maintenance manuals as appropriate. 2. Inspect physical, electrical, and mechanical condition including evidence of moisture or corona. 3. Inspect anchorage, alignment, grounding, and required area clearances around switchboard. 4. Clean the unit. 5. Complete inspection tasks and maintenance items indicated in the Electrical Switchgear and Switchboard Assemblies Report. 6. Confirm correct operation and sequencing of electrical and mechanical interlock systems. Attempt closure on locked-open devices. Attempt to open locked-closed devices. Make key exchange with all devices included in the interlock scheme as applicable. 7. Use appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. See maintenance manual for proper lubricant. 8. Verify correct barrier and shutter installation and operation. 9. Molded-case and insulated-case circuit breakers. a. Operate to ensure smooth operation. b. Inspect operating mechanism, contacts, and arc chutes in unsealed units. 10. Inspect mechanical indicating devices for correct operation. 11. Verify that vents are clear. 12. Perform visual and mechanical inspection of instrument transformers. a. Inspect physical and mechanical condition. b. Clean the unit. c. Verify that all required grounding and shorting connections provide contact. d. Verify correct operation of transformer withdrawal mechanism and grounding operation, if applicable. e. Use appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. 13. Inspect control power transformers. a. Inspect for physical damage, cracked insulation, broken leads, tightness of connections, defective wiring, and overall general condition. b. Verify correct functioning of drawout disconnecting and grounding contacts and interlocks. 14. Place switchboard back in service. 15. Attach electronic copy of report to PM work request record in FMMS. | COMS_ELEC
COMS-ELEC-120A | 1. Consult manufacturers' operation and maintenance manuals as appropriate. 2. Inspect physical, electrical, and mechanical condition including evidence of moisture or corona. 3. Inspect anchorage, alignment, grounding, and required area clearances around switchboard. 4. Clean the unit. 5. Complete inspection tasks and maintenance items indicated in the Electrical Switchgear and Switchboard Assemblies Report. 6. Confirm correct operation and sequencing of electrical and mechanical interlock systems. Attempt closure on locked-open devices. Attempt to open locked-closed devices. Make key exchange with all devices included in the interlock scheme as applicable. 7. Use appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. See maintenance manual for proper lubricant. 8. Verify correct barrier and shutter installation and operation. 9. Exercise all active components. 10. Inspect mechanical indicating devices for correct operation. 11. Verify that vents are clear. 12. Perform visual and mechanical inspection of instrument transformers. a. Inspect physical and mechanical condition. b. Clean the unit. c. Verify that all required grounding and shorting connections provide contact. d. Verify correct operation of transformer withdrawal mechanism and grounding operation, if applicable. e. Use appropriate lubrication on moving current-carrying parts and on moving and sliding surfaces. 13. Inspect control power transformers. a. Inspect for physical damage, cracked insulation, broken leads, tightness of connections, defective wiring, and overall general condition. b. Verify correct functioning of drawout disconnecting and grounding contacts and interlocks. 14. Place switchboard back in service. 15. Attach electronic copy of report to PM work request record in FMMS. | COMS_ELEC
COMS-ELEC-125A | 1. Inspect physical, electrical, and mechanical condition, including evidence of moisture or corona. 2. Inspect anchorage, alignment, grounding, and required clearances. 3. Clean the insulators. 4. Verify correct blade alignment, blade penetration, travel stops, arc interrupter operation, and mechanical operation. 5. Verify that each fuseholder has adequate mechanical support and contact integrity. 6. Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer’s published data or NETA MTS 2011, Table 100.12. 7. Perform a thermographic survey if de-energization is not possible. 8. Verify operation and sequencing of interlocking systems. 9. Perform a series of three opening/closing operations 10. Clean area around the equipment. 11. Complete work order data. | COMS_ELEC
COMS-ELEC-125B | 1. Disconnect power supply to battery charger. 2. Remove old batteries from service. 3. Install new batteries. 4. Apply No-OX to battery terminals. 5. Connect power supply to new batteries. 6. Test for proper voltage after installation of new batteries. 7. Clean area around the equipment. 8. Complete work order data. | COMS_ELEC
COMS-ELEC-126B | 1. Inspect physical, electrical, and mechanical condition including evidence of moisture or corona. 2. Inspect anchorage, alignment, grounding, and required clearances. 3. Clean the unit including insulating surfaces. 4. Verify that each fuseholder has adequate mechanical support and contact integrity. 5. Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer’s published data or NETA MTS 2011, Table 100.12. 6. Perform a thermographic survey if de-energization is not possible. 7. Verify correct barrier and shutter installation and operation. 8. Clean area around the equipment. 9. Complete work order data. | COMS_ELEC-LINE
COMS-ELEC-130A | 1. Inspection and testing must be performed by a NETA certified company. 2. Racking of circuit breakers must be performed by COMS contractor. Bolt-in type circuit breakers must be removed and re-installed by company performing inspection and testing. 3. Perform visual and mechanical inspections as stipulated by the lastest edition of ANSI/NETA MTS (Standard for Maintenance Testing Specifications) Sec 7.6.2.3.1 - Circuit Breakers, Medium Voltage, Vacuum. 4. Perform testing as indicated in latest operations and maintenance manual. The following manuals were in affect as of the writing of this procedure. 4a. Bldg 300 and 304 -- Square-D bulletin 6055-31 (E-gap and contact erosion, hi-pot, resistance measurements) 4b. Substations A and B -- Eaton bulletin IB131006EN (Insulation integrity, vacuum integrity, contact erosion and wipe, closure test) 4c. Main Substation -- ABB bulletin IB 1VAF101229 (Primary insulation integrity, vacuum integrity, contact resistance testing) 4d. Substation 8 -- Siemens SG-3268-02 (Contact erosion, spring charging check, vacuum integrity, insulation and contact resistance) 5. Lubricate in accordance with appropriate manuals above. 6. Maintain a maintenance log for each circuit breaker. 7. Clean area around the equipment. 8. Complete work order data. | COMS_ELEC-LINE
COMS-ELEC-130B | 1. Inspection and testing must be performed by a NETA certified company. 2. Racking of circuit breakers must be performed by COMS contractor. Bolt-in type circuit breakers must be removed and re-installed by company performing inspection and testing. 3. Perform visual and mechanical inspections as stipulated by the lastest edition of ANSI/NETA MTS (Standard for Maintenance Testing Specifications) Sec 7.6.2.3.1 - Circuit Breakers, Medium Voltage, Vacuum. 4. Perform testing as indicated in latest operations and maintenance manual. The following manuals were in affect as of the writing of this procedure. 4a. Bldg 300 and 304 -- Square-D bulletin 6055-31 (E-gap and contact erosion, hi-pot, resistance measurements) 4b. Substations A and B -- Eaton bulletin IB131006EN (Insulation integrity, vacuum integrity, contact erosion and wipe, closure test) 4c. Main Substation -- ABB bulletin IB 1VAF101229 (Primary insulation integrity, vacuum integrity, contact resistance testing) 4d. Substation 8 -- Siemens SG-3268-02 (Contact erosion, spring charging check, vacuum integrity, insulation and contact resistance) 5. Lubricate in accordance with appropriate manuals above. 6. Maintain a maintenance log for each circuit breaker. 7. Clean area around the equipment. 8. Complete work order data. | COMS_ELEC
COMS-ELEC-131A | 1. Refer to S&C Instruction Sheet 731-503. 2. Visually inspect for excessive corrosion at terminal pads; discoloration, contamination, or other damage to pole-unit insulation; excessive terminal pad loading; excessive corrosion or water ingress inside control cabinet. 3. Verify that the gas-pressure gauge is in the white "OK TO OPERATE" zone. Corrective actions are required if gauge is in either yellow or red zones. 4. Manual Trip Device and Trip Energy Supply 4a. Verify proper condition of the manual trip device. Crank it 5 to 10 times and check that red LED is flashing. 4b. Verify that the trip energy supply is storing energy. Open the swingout panel to access the circuit board of the trip-energy supply. Press the push button on the trip-energy supply’s circuit board. See Figure 24. If the trip energy supply is functioning properly, the red LED on the board will light continuously. 5. Make sure the test switch cover is in place and secure. Make sure the pins are removed from the CT shorting blocks. | COMS_ELEC-LINE
COMS-ELEC-135A | 1. Check with operating or area personnel for deficiencies. 2. Inspect wiring, wiring connections, and fuse blocks for looseness, charring, evidence of short circuiting, overheating. 3. Inspect general condition of equipment and clean exterior and surrounding area. 4. Perform complete operational testing. 5. Clean area around the equipment. 6. Complete work order data. | COMS_ELEC-LINE
COMS-ELEC-200A | 1. Consult manufacturers' operation and maintenance manuals as appropriate. 2. Perform inspections and measurements as indicated on the Dry-Type Transformer Inspection Report. 3. Attach electronic copy of report to PM work request record in FMMS. 4.Clean area around the equipment. 5. Complete work order data. | COMS_ELEC
COMS-ELEC-200M | 1. Examine the exterior of the transformer for any damage, cracks, rust or leaks; check around bushings, gaskets and pressure relief device . 2. Take temperature readings of coils using an infrared camera. Record readings. 3. Check for signs of moisture or overheating. 4. Record all gauge and indicator readings. 5. Clean area around the equipment. 6. Complete work order data. | COMS_ELEC-LINE
COMS-ELEC-200Q | 1. Examine the exterior of the transformer for any damage, cracks, rust or leaks; check around bushings, gaskets and pressure relief device . 2. Take temperature readings of coils using an infrared camera. Record readings. 3. Check for signs of moisture or overheating. 4. Record all gauge and indicator readings. 5. Clean area around the equipment. 6. Complete work order data. | COMS_ELEC-LINE
COMS-ELEC-201A | 1. Consult manufacturers' operation and maintenance manuals as appropriate. 2. Perform inspections and measurements as indicated on the Liquid-Filled Transformer Inspection Report. 3. Attach electronic copy of report to PM work request record in FMMS. 4. Clean area around the equipment. 5. Complete work order data. | COMS_ELEC
COMS-ELEC-201B | 1. This biennial PM must be performed starting with the first year of the contract. 2. Perform the inspections and tests stipulated by the latest edition of ANSI/NETA MTS (Standard for Maintenance Testing Specifications) Sec 7.2.2 - Transformer, Liquid-Filled (Visual, Mechanical, and Electrical Testing (excluding optional tests)). 3. A report signed and sealed by a Professional Engineer shall be submitted for each transformer tested. | COMS_ELEC
COMS-ELEC-201M | 1. Examine the exterior of the transformer for any damage, cracks, rust or leaks; check around bushings, gaskets and pressure relief device. 2. Check and record the oil level, pressure and temperature readings. Take maximum temperature readings if equipped with Max Temp Indicator (Reset indicator). 3. Check fans, motors and other auxiliary devices for proper operation; where applicable. 4. Take primary and secondary voltage readings. Record readings. 5. Take secondary currents readings where safe and possible. 6. Clean transformer exterior and the surrounding area. 7. Complete work order data. | COMS_ELEC
COMS-ELEC-301A | **Note: Annual PM must be performed in conjunction with Semiannual PM (ELEC-301S). 1. Replace battery 2. Clean area around the equipment. 3. Complete work order data. | COMS_ELEC
COMS-ELEC-301S | 1. Press test button for a minimum of 30 seconds and ensure light is operating properly. 2. Check that the charger is operating properly. 3. Check for any signs of corrosion on the battery terminals or wires. 4. Clean battery terminals, area around batteries, and exterior of light fixture. 5. Complete work order data. | COMS_ELEC
COMS-ELEC-901O | 1. Perform the tests stipulated by the lastest edition of ANSI/NETA MTS (Standard for Maintenance Testing Specifications) Sec 7.3.3.1 - Cables, Medium and High-Voltage Visual & Mechanical Inspection. Also, perform a Partial Discharge On Line or Off line. These inspections are to be performed on the section of underground cable emanating from the equipment that this PM is associated with. 2. A report signed and sealed by Professional Engineer shall be submitted for each cable tested. | COMS_ELEC
COMS-ELEC-902O | This PM must be performed during the first and fourth year of the contract. 1. Perform the tests stipulated by the lastest edition of ANSI/NETA MTS (Standard for Maintenance Testing Specifications) Sec 7.9.1 - Protective Relays, Electromechanical and Solid State; Sec 7.9.2 - Protective Relays, Microprocessor Based; Sec 7.10 - Instrument Transformers. 2. A report signed and sealed by Professional Engineer shall be submitted for each site tested. | COMS_ELEC-LINE
COMS-ELEV-001A | 1. Perform periodic tests as required by the applicable version of ASME A17.1 and ASME A17.2. 2. Provide documentation of tests, including reports and certification from the State-certified inspector as well as any deficiencies identified. | COMS_SUB_ELEV
COMS-ELEV-001Q | 1. Ride car, checking for any unusual noise or operation. 2. In car: inspect and clean fixtures and signal in operating panel and car position and direction indicator. 3. In car: check operation of emergency lights, bell, handrails, ceiling panels and hang on panels for tightness. Check fire alarm devices. 4. In car: check for tripping hazards. 5. Inspect and lubricate rails of hoistway. 6. Examine all wire rope and fastenings, traveling cables, counterweights and compensators. 7. Hallway corridor: inspect hall buttons, signal lamps, lanterns, hall position indicator, starter station, key operation and lamps. 8. Motor room: inspect and maintain as necessary all machine room equipment, tank oil level and lockout and log record. 9. Motor room: inspect and adjust controller contacts; main operating contactors and switches. 10. Motor room: inspect pump and valve unit for leaks. 11. Check and maintain quantity and quality of oil in all reservoirs. 12. Examine, clean and adjust breaks as necessary. 13. Hatch: inspect door operator; clean and lubricate chain and belt tension. 14. Hatch: inspect door, clean and adjust safety edge, light ray and cables. 15. Hatch: clean and adjust proximity devices on door. 16. Inspect pit gland packing. 17. Clean equipment and surrounding area. 18. Complete work order data. | COMS_SUB_ELEV
COMS-ELEV-001S | 1. Perform periodic inspections as required by the applicable version of ASME A17.1 and ASME A17.2. 2. Provide documentation of inspections, including reports and certification from the State-certified inspector as well as any deficiencies identified. | COMS_SUB_ELEV
COMS-ELEV-002A | *This PM must be performed in conjunction with Monthly, Quarterly, and Semiannual PM.* 1. Perform periodic tests as required by the applicable version of ASME A17.1 and ASME A17.2. 2. Provide documentation of tests, including reports and certification from the State-certified inspector as well as any deficiencies identified. 3. Check and adjust scavenger pump as needed. 4. Check and perform test on bypass valve. 5. Check traveling hitches for any rubbing. 6. Check and clean guide rails. 7. Check operation of main line disconnects. 8. Check and test Fire Recall. 9. Check emergency power operation. 10. Test Shunt Trip operation. 11. Perform annual no-load tests via Inspector. 12. Test Pipe Rupture Valve. 13. Check floor to floor travel times, adjust as needed. 14. Replace filter on hydraulic system and check for contaminants. 15. Pull SD card, upload the log file, clear log file, email file to COR. 16. Clean area around the equipment, elevator mechanical room, etc. 17. Complete work order data. | COMS_SUB_ELEV
COMS-ELEV-002M | 1. Check with operating personnel for any deficiencies. 2. Ride car, checking for any unusual noise or operation. 3. Check controller for operation. 4. Check controller AC unit for proper operation and clean filters. 5. Check door operation; adjust and clean sills. 6. Check pump unit oil levels and check for leaks, clean as necessary. 7. Check and test operation of hoistway sump pumps. 8. Check with operating personnel for any deficiencies. 9. Check controller monitor for Event History and record in report 10. Check controller bulbs for proper illumination 11. Enuse G.A.L controller fuses are in workiing condition 12. Motor room: inspect and maintain as necessary all machine room equipment, tank oil level and lockout and log record. 13. Ride car, checking for any unusual noise or operation. 14. Clean equipment, machine room and surrounding area. 15. Check car for leveling at every floor 16. In car: check operation of emergency lights, bell, handrails, ceiling panels and hang on panels for tightness. Check fire alarm devices. 17. Check ICU operation, and clean covers. 18. Check button operations and ensure no sticking. 19. Clean area around the equipment, elevator mechanical room, etc. 20. Complete work order data. | COMS_SUB_ELEV
COMS-ELEV-002Q | *This PM must be performed in conjunction with Monthly PM.* 1. In car: inspect and clean fixtures and signal in operating panel and car position and direction indicator. 2. In car: check for tripping hazards. 3. Inspect and lubricate rails of hoistway. 4. Examine all wire rope and fastenings, traveling cables, counterweights and compensators. 5. Hallway corridor: inspect hall buttons, signal lamps, lanterns, hall position indicator, starter station, key operation and lamps. 6. Motor room: inspect and adjust controller contacts; main operating contactors and switches. 7. Motor room: inspect pump and valve unit for leaks. 8. Check and maintain quantity and quality of oil in all reservoirs. 9. Examine, clean and adjust breaks as necessary. 10. Hatch: inspect door operator; clean and lubricate chain and belt tension. 11. Hatch: inspect door, clean and adjust safety edge, light ray and cables. 12. Hatch: clean and adjust proximity devices on door. 13. Inspect pit gland packing. 14. Clean and lubricate car door tracks and gate switch. 15. Check and repair door closers and gibs. 16. Check interlocks and adjust as needed. 17. Check, clean, and lubricate roller guides; adjust as necessary. 18. Clean area around the equipment, elevator mechanical room, etc. 19. Complete work order data. | COMS_SUB_ELEV
COMS-ELEV-002S | *This PM must be performed in conjunction with Monthly & Quarterly PM.* 1. Perform periodic tests as required by the applicable version of ASME A17.1 and ASME A17.2. 2. Clean and lubricate fan in car. 3. Clean and lubricate door tracks on hatch. 4. Clean and check motor belts, adjust as necessary on pump unit. 5. Check operation of oil cooler on pump unit. 6. Check and clean filter screens, including down close valve, on pump unit. 7. Check packing for leaking in hoistway. 8. Check limit switches, lubricate and adjust for proper clearances. 9. Check door open and close time, adjust as needed 10. Clean area around the equipment, elevator mechanical room, etc. 11. Complete work order data. | COMS_SUB_ELEV
COMS-ENV-007A | 1. Inspect spill kits for integrity. Check for cracks, ripped covers, moisture, and overall condition. 2. Inspect contents of spill kits to ensure it is properly stocked. 3. Ensure spill kits are properly labeled. 3. Place service call for replacing of spill kits that are damaged/unusable or in need of replenishment. 4. Document findings on WR. | COMS_ENV SPEC
COMS-ENV-008S | 1. Remove old wet boom from stream. 2. Place new boom(s) in stream. 3. Secure boom(s) in place with new rope and/or stakes. 4. Dispose of spent spill booms as routine waste unless contaminated with fuel or oil. If boom is contaminated with excessive amounts of fuel, oil or hydraulic fluid, perform the following: 5. Notify COR or FAA-designated personnel. 6. Take contaminated boom to Building 56. 7. Profile, store and dispose of contaminated boom as appropriate. | COMS_ENV SPEC
COMS-FA-001S | 1. Visually inspect all alarm equipment connected to the Control Equipment, including initiation devices for obstructions or physical damage, clean dirt and dust from interior and exterior of panel/pull boxes, tighten loose connections. 2. Notify cognizant personnel prior to testing. 3. Conduct operational test of initiating and signal transmitting devices in populated buildings by building zone/area. 4. For those circuits which do not operate properly, check detectors, pull stations, control units for dust or defective components; make minor adjustments as required. 5. Check battery voltages where installed; replace as required. 6. Conduct operational test of 10% of total number of spot type heat detectors and all smoke detectors. 7. For those circuits which do not operate properly, check to determine if problem relates to circuit, device, or control unit, make minor adjustments as required. 8. Replace if detector is defective but if no replacement is immediately available, remove detector, re-establish initiating circuit and tag location until a replacement detector is installed. 9. Restore system to proper operating condition and notify personnel upon completion of tests. 10. Clean area around the equipment 11. Complete work order data. | COMS_FIRE INSPEC
COMS-FA-002S | 1. Visually inspect all annunciating devices for obstructions or physical damage, clean dirt and dust device. 2. Notify cogniant personnel prior to testing. 3. Conduct operational test of annunciating devices. 4. For those circuits which do not operate properly, check to determine if problem relates to circuit, device, or control unit, make minor adjustments as required. 5. Replace if device is defective but if no replacement is immediately available, remove device, re-establish initiating circuit and tag location until a replacement is installed. 6. Restore system to proper operating condition and notify personnel upon completion of tests. 7. Clean area around the equipment 8. Complete work order data. | COMS_FIRE INSPEC
COMS-FA-006S | 1. Inform all appropriate personnel of intention to work on the flame detectors. 2. Disable any automatic systems that may be activated by the flame detectors if not required as part of the maintenance check. 3. Check that the control panel for the detectors is functioning correctly and shows no faults. 4. Inspect the detector-viewing window for any build-up of dust or other contaminants on the optical surface. If necessary, clean the optical surface according to manufacturer instructions.. 5. Ensure the detector still has a clear line of sight of the area it is protecting and no obstacles obstuct its view. 6. Check that the detector is securely fitted. 7. Visually check the exterior of the detector for any mechanical or corrosive damage. 8. Test the operation of the detector according to manufacturers instructions and the proper signal is transmitted to the fire alarm control panel. 9. Reinstate any automatic system disabled during maintenance. 10. Inform all appropriate personnel on completion of the maintenance work and if necessary record this work. 11. Clean area around the equipment 12. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-001A | **Perform In Conjunction With Monthly and Semi-Annual PM** 1. Blow out entire system to make sure that the system is not plugged or restricted. 2. Run out hose reels and check hoses. 3. Conduct operational test of actuating devices, both automatic, manual and alarm system. 4. Prior to conducting tests, close valves, disable CO2 dumping control and manually override computer shutdown feature if applicable, all in accordance with the manufacturers specifications. 5. Check the operation and timing of the time delay control and check operation of the abort station. 6. Restore system to proper operating condition and notify personnel upon completion of tests. 7. Clean area around the equipment 8. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-001M | 1. Check that nozzles, heads and hand hose lines are clear from obstructions, have not been damaged and in proper position. 2. Check to ensure that all operating controls are properly set. 3. Clean nozzles as required. 4. Visually inspect the control panel for obstructions or physical damage; clean dirt and dust from interior and exterior, make sure that all cards are plugged in tightly, tighten loose connections and make other minor adjustments as necessary. 5. Check battery voltages where installed. 6. Clean up around system. 7. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-001S | **Perform In Conjunction With Monthly PM** 1. Weigh CO2 cylinders; replace any that show a weight loss greater than 10%. 2. Clean area around the equipment 3. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-002A | **Note: Annual PM must be performed in conjunction with Monthly and Semiannual PMs 1. Check pressure and condition of tank(s), note and correct any deficiencies 1. Check pressure and condition of tank(s), note and correct any deficiencies 2. Blow out entire system to make sure that the piping and nozzles are not plugged or restricted. 3. Conduct operational test of actuating devices, both automatic, manual and alarm system. 4. Prior to conducting tests disable Clean Agent dumping control and manually override computer shutdown feature if applicable, all in accordance with the manufacturers specifications. 5. Check the operation and timing of the time delay control and check operation of the abort station. 6. Restore system to proper operating condition and notify personnel upon completion of tests. 7. Clean area around the equipment 8. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-002M | 1. Check that nozzles have not been damaged and in proper position. 2. Check to ensure that all operating controls are properly set. 3. Clean nozzles as required. 4. Visually inspect the control panel for obstructions or physical damage; clean dirt and dust from interior and exterior, make sure that all cards are plugged in tightly, tighten loose connections and make other minor adjustments as necessary. 5. Check battery voltages where installed, recharge or replace as required. 6. Clean up around system. 7. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-002S | **Note: Semiannual PM must be performed in conjunction with Monthly PM 1. Check pressure and condition of tank(s), note and correct any deficiencies. 2. Check pressure and condition of tank(s), note and correct any deficiencies. 3. Clean area around the equipment 4. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-003A | **Note: Annual PM must be performed in conjunction with Monthly and Semiannual PMs 1. Test all actuating and operating devices; turn valve on dry chemical bottle or cylinder to off position in accordance with manufacturers specifications. 2. Test operation of control head by removing fusible link, activating the detectors or pulling test control. Restore system to normal operation and make minor adjustments as applicable. 3. Open and check dry chemical in cylinder and stored pressure systems to ensure it is free flowing and without lumps. 4. When an alarm system is reactivated, ensure that it functions in accordance with manufacturers specifications. 5. Clean area around the equipment 6. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-003M | 1. Check nozzles, heads, and fusible links or heat detectors to ensure that they are clean, have adequate clearance from obstructions and have not been damaged. 2. Check hand hose lines, if applicable, to ensure that they are clear, in proper position and in good condition. 3. Check to ensure that all operating controls are properly set. 4. Observe pressure on system to ensure that proper pressure is maintained. 5. Clean area around system. 6. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-003S | **Note: Semiannual PM must be performed in conjunction with Monthly PM 1. Check expellant gas cylinders of gas cartridge systems for proper pressure or weight to ensure that sufficient gas is available. 2. Clean area around the equipment 3. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-004A | **NOTE: Maintenance shall be performed in conjunction with Monthly and Quarterly PMs 1. Open and close post indicator valve to check operation; make minor repairs such as lubricating valve stem, cleaning target windows as required. 2. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 3. Perform operational test of water flow detectors; make minor adjustments and restore system to proper operating condition. 4. Check general condition of sprinklers and sprinkler system; make minor adjustments as required. 5. Check equipment gaskets, piping, packing glands, and valves for leaks; tighten flange bolts and loose connections to stop all leaks. 6. Check condition of fire department connections; replace missing or broken covers as required. 7. Trip test dry pipe system using test valve furthest from dry pipe valve (control valve partially open); make minor adjustments as necessary and restore system to fully operational condition. 8. Check operation of quick opening device. 9. Clean area around the equipment 10. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-004M | 1. Notify proper authorities prior to testing any alarm systems. 2. Check to ensure that alarm drain is open; clean drain line if necessary. 3. Open water motor alarm test valve and ensure that outside alarm operates; lubricate alarm, make adjustments as required. 4. Visually check water pressure to ensure that adequate operating pressure is available; make adjustments as required. 5. Visually check system air pressure; pump up system and make minor adjustments as required. 6. Inspect OS&Y and PIV cut-off valves for open position. 7. Clean area around the equipment 8. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-004Q | **NOTE: Maintenance shall be performed in conjunction with Monthly PM 1. Conduct main drain test by opening 2" test valve; maintain a continuous record of drain tests; make minor adjustments if applicable; restore system to proper operating condition. 2. Clean area around system components. 3. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-005A | 1. Notify proper authorities prior to testing any alarm systems. 2. Open and close post indicator valve (PIV) to check operation; make minor repairs such as lubricating valve stem, cleaning and/or replacing target windows as required. 3. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems, tightening packing glands as required. 4. Perform operational test of water flow detectors; make minor adjustments and restore system to proper operating condition. 5. Check to ensure that alarm drain is open; clean drain line if necessary. 6. Open water motor alarm test valve and ensure that outside alarm operates; lubricate alarm, make adjustments as required. 7. Conduct main drain test by opening 2" test valve; maintain a continuous record of drain tests; make minor adjustments if applicable; restore system to proper operating condition. 8. Check general condition of sprinklers and sprinkler system; make minor adjustments as required. 9. Check equipment gaskets, piping, packing glands, and valves for leaks; tighten flange bolts and loose connections to stop all leaks. 10. Check condition of fire department connections; replace missing or broken covers as required. 11. Trip test wet pipe system using test valve furthest from wet pipe valve (control valve); make minor adjustments as necessary and restore system to proper operating condition. 12. Inspect OS&Y and PIV cut-off valves for open position. 13. Clean area around system components. 14. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-005Q | 1. Notify proper authorities prior to testing any alarm systems. 2. Check to ensure that alarm drain is open; clean drain line if necessary. 3. Open water motor alarm test valve and ensure that outside alarm operates; lubricate alarm, make adjustments as required. 4. Conduct main drain test by opening 2" test valve; maintain a continuous record of drain tests; make minor adjustments if applicable; restore system to proper operating condition. 5. Inspect OS&Y and PIV cut-off valves for open position. 6. Clean area around system components. 7. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-006A | 1. Remove hydrant caps and check condition of gaskets; replace as required. 2. Flush hydrant, lubricate cap threads and reinstall cap. 3. Clean area around the equipment 4. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-007S | 1. Remove set screw, cap and wire seal. 2. Apply lubricant to threads, open and close valve. 3. Check operation of and sign and clean glass indicator windows. 4. Install cap and tighten screw, install handle and wire seal with valve open. 5. Clean valve exterior and area around valve. 6. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-008A |  | COMS_FIRE INSPEC
COMS-FP-008M | Inspect fire extinguisher to verify: 1. Proper type. 2. Location in designated place. 3. No obstruction to access or visibility. 4. Operating instructions on nameplate legible and facing outward. 5. Safety seals and tamper indicators not broken or missing. 6. Fullness determined by weighing or "hefting". 7. Examination for obvious physical damage, corrosion, leakage, or clogged nozzle. 8. Pressure gauge reading or indicator in the operable range or position. 9. HMIS label in place. 10. Take corrective action to replace deficiencies listed in 2., 3., and 9.. 11. Perform maintenance procedures to correct deficiencies listed in 4., 5., 6., 7., and 8. for rechargeable fire extinguishers. 12. Remove, discharge, destroy, or return to manufacturer nonrechargeable extinguishers with deficiencies listed in 4., 6., 7. and 8. 13. Clean area around the equipment 14. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-008O | 1. Perform hydrostatic test. 2. Ensure date of test is clearly labeled on fire extinguisher and work request. 3. Document all required information on work request. | COMS_FIRE INSPEC
COMS-FP-009A | 1. After ensuring all valves relating to water system are in correct position open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 2. Controller panel: check controller panel for proper operation in accordance with standard procedures for the type of panel installed, replace burned out bulbs and fuses; check wiring for loose connections and fraying; make other repairs as necessary. 3. Diesel engine: drain and replace engine oil and oil filter. 4. Diesel engine: drain and replace radiator coolant. 5. Diesel engine: check battery water level; add water if low. 6. Diesel engine: check battery terminals for corrosion; clean if necessary. 7. Diesel engine: check belts for tension and wear; adjust or replace if required. 8. Diesel engine: check fuel level in tank; refill as required. 9. Diesel engine: check electrical wiring, connections, switches, etc.; adjust or tighten as necessary. 10. Diesel engine: perform 10 minute pump check for proper operation and adjust as required. 11. Centrifugal pump: check for leaks on suction and discharge piping, seals, packing glands, etc. 12. Centrifugal pump: check pump operation; vibration, noise overheating, etc. 13. Centrifugal pump: check alignment, clearances, and rotation of shaft and coupler (includes removing and reinstalling safety cover). 14. Centrifugal pump: tighten or replace loose, missing or damaged nuts, bolts, or screws. 15. Centrifugal pump: lubricate pump as required. 16. Centrifugal pump: check suction or discharge pressure gauge readings and flow rate. 17. Centrifugal pump: check packing glands and tighten or repack as required; note that slight dripping is required for proper lubrication of shaft. 18. Inspect and clean strainers after each use and flow test. 19. Clean equipment and surrounding area. 20. Complete work order data. | COMS_EQUIP MECH
COMS-FP-009M | 1. Ensure all valves relating to water system are in correct position. 2. Diesel engine: check oil level in crankcase with dipstick; add oil as necessary. 3. Diesel engine: check radiator coolant level; add water if low. 4. Diesel engine: perform 10 minute pump check for proper operation and adjust as required. 5. Inspect and clean strainers after each use and flow test. 6. Clean equipment and surrounding area. 7. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-009S | 1. After ensuring all valves relating to water system are in correct position open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 2. Controller panel: check controller panel for proper operation in accordance with standard procedures for the type of panel installed, replace burned out bulbs and fuses; check wiring for loose connections and fraying; make other repairs as necessary. 3. Diesel engine: check oil level in crankcase with dipstick; add oil as necessary. 4. Diesel engine: check radiator coolant level; add water if low. 5. Diesel engine: check battery water level; add water if low. 6. Diesel engine: check battery terminals for corrosion; clean if necessary. 7. Diesel engine: check belts for tension and wear; adjust or replace if required. 8. Diesel engine: check fuel level in tank; refill as required. 9. Diesel engine: check electrical wiring, connections, switches, etc.; adjust or tighten as necessary. 10. Diesel engine: perform 10 minute pump check for proper operation and adjust as required. 11. Centrifugal pump: check for leaks on suction and discharge piping, seals, packing glands, etc. 12. Centrifugal pump: check pump operation; vibration, noise overheating, etc. 13. Centrifugal pump: check alignment, clearances, and rotation of shaft and coupler (includes removing and reinstalling safety cover). 14. Centrifugal pump: tighten or replace loose, missing or damaged nuts, bolts, or screws. 15. Centrifugal pump: lubricate pump as required. 16. Centrifugal pump: check suction or discharge pressure gauge readings and flow rate. 17. Centrifugal pump: check packing glands and tighten or repack as required; note that slight dripping is required for proper lubrication of shaft. 18. Inspect and clean strainers after each use and flow test. 19. Clean equipment and surrounding area. 20. Complete work order data. | COMS_EQUIP MECH
COMS-FP-010O | 1. Perform hydro static test. 2. Ensure date of test is clearly labeled on fire extinguisher and work request. 3. Document all required information on work request. | COMS_FIRE INSPEC
COMS-FP-010S | 1. After ensuring all valves relating to water system are in correct position open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 2. Controller panel: check controller panel for proper operation in accordance with standard procedures for the type of panel installed, replace burned out bulbs and fuses; check wiring for loose connections and fraying; make other repairs as necessary. 3. Diesel engine: check oil level in crankcase with dipstick; add oil as necessary. 4. Diesel engine: check radiator coolant level; add water if low. 5. Diesel engine: check battery water level; add water if low. 6. Diesel engine: check battery terminals for corrosion; clean if necessary. 7. Diesel engine: check belts for tension and wear; adjust or replace if required. 8. Diesel engine: check fuel level in tank; refill as required. 9. Diesel engine: check electrical wiring, connections, switches, etc.; adjust or tighten as necessary. 10. Diesel engine: perform 10 minute pump check for proper operation and adjust as required. 11. Centrifugal pump: check for leaks on suction and discharge piping, seals, packing glands, etc. 12. Centrifugal pump: check pump operation; vibration, noise overheating, etc. 13. Centrifugal pump: check alignment, clearances, and rotation of shaft and coupler (includes removing and reinstalling safety cover). 14. Centrifugal pump: tighten or replace loose, missing or damaged nuts, bolts, or screws. 15. Centrifugal pump: lubricate pump as required. 16. Centrifugal pump: check suction or discharge pressure gauge readings and flow rate. 17. Centrifugal pump: check packing glands and tighten or repack as required; note that slight dripping is required for proper lubrication of shaft. 18. Inspect and clean strainers after each use and flow test. 19. Clean equipment and surrounding area. 20. Complete work order data. Coordinate w/Motor Pool | COMS_FIRE INSPEC
COMS-FP-011M | 1. Check foam concentrate level in tank; add concentrate as required to maintain proper level. 2. Ensure all valves relating to foam/water system are in correct position. 3. Visually check proportioning device, pumps, and foam nozzles; correct any observed deficiencies. 4. Check water supply pressure; adjust as necessary/ 5. Centrifugal pump: test start pump without foam discharger. 6. Inspect and clean strainers after each use and flow test. 7. Clean equipment and surrounding area. 8. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-011Q | 1. Check foam concentrate level in tank; add concentrate as required to maintain proper level. 2. Ensure all valves relating to foam/water system are in correct position. 3. Visually check proportioning device, pumps, and foam nozzles; correct any observed deficiencies. 4. Check water supply pressure; adjust as necessary/ 5. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 6. Centrifugal pump: perform 10 minute pump test run, check for proper operation and adjust as required. 7. Centrifugal pump: test start pump without foam discharger. 8. Centrifugal pump: check for leaks on suction and discharge piping, seals, packing glands, etc. 9. Centrifugal pump: check for excessive vibration, noise, overheating, etc. 10. Centrifugal pump: check alignment, clearances, and rotation of shaft and coupler (includes removing and reinstalling safety cover). 11. Centrifugal pump: tighten or replace loose, missing or damaged nuts, bolts, or screws. 12. Centrifugal pump: lubricate pump and motor as required. 13. Centrifugal pump: check suction or discharge pressure gauge readings and flow rate. 14. Centrifugal pump: check packing glands and tighten or repack as required; note that slight dripping is required for proper lubrication of shaft. 15. Inspect and clean strainers after each use and flow test. 16. Clean equipment and surrounding area. 17. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-012A | **Annual PM Procedure must be performed in conjunction with Quarterly PM 1. Notify proper authorities prior to testing any alarm systems. 2. Open and close post indicator valve (PIV) to check operation; make minor repairs such as lubricating valve stem, cleaning and/or replacing target windows as required. 3. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems, tightening packing glands as required. 4. Perform operational test of water flow detectors; make minor adjustments and restore system to proper operating condition. 5. Check general condition of sprinklers and sprinkler system; make minor adjustments as required. 6. Check equipment gaskets, piping, packing glands, and valves for leaks; tighten flange bolts and loose connections to stop all leaks. 7. Check condition of fire department connections; replace missing or broken covers as required. 8. Clean area around the equipment 9. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-012Q | 1. Notify proper authorities prior to testing any alarm systems. 2. Check to ensure that alarm drain is open; clean drain line if necessary. 3. Open water motor alarm test valve and ensure that outside alarm operates; lubricate alarm, make adjustments as required. 4. Conduct main drain test by opening 2" test valve; maintain a continuous record of drain tests; make minor adjustments if applicable; restore system to proper operating condition. 5. Inspect OS&Y and PIV cut-off valves for open position. 6. Clean area around system components. 7. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-014S | 1. Remove set screw, cap and wire seal. 2. Lubricate stem; open and close valve to check position. 3. Check packing gland for leaks; tighten packing and flange bolts as required. 4. Install cap and tighten screw, install handle and wire seal with valve open. 5. Clean valve exterior and area around valve. 6. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-015A | 1. Notify proper authorities prior to testing any alarm systems. 2. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 3. Check general condition of standpipe system; make minor adjustments as required. 4. Check equipment gaskets, piping, packing glands, and valves for leaks; tighten flange bolts and loose connections to stop all leaks. 5. Check condition of fire hose; replace missing or leaking hose as required. 6. Restore system to proper operating condition. 7. Inspect OS&Y cut-off valves for open position. 8. Clean area around system components. 9. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-015M | 1. Notify proper authorities prior to testing any alarm systems. 2. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 3. Inspect OS&Y cut-off valves for open position. 4. Clean area around system components. 5. Complete work order data. | COMS_FIRE INSPEC
COMS-FP-017M | 1. Check foam concentrate level in tank; add concentrate as required to maintain proper level. 2. Ensure all valves relating to foam/water system are in correct position. 3. Visually check proportioning device, pumps, and foam nozzles; correct any observed deficiencies. 4. Check water supply pressure; adjust as necessary/ 5. Open and close OS&Y (outside stem and yoke) cut-off valve to check operation; make minor repairs such as lubricating stems and tightening packing glands as required. 6. Centrifugal pump: perform 10 minute pump test run, check for proper operation and adjust as required. 7. Centrifugal pump: test start pump without foam discharger. 8. Centrifugal pump: check for leaks on suction and discharge piping, seals, packing glands, etc. 9. Centrifugal pump: check for excessive vibration, noise, overheating, etc. 10. Centrifugal pump: check alignment, clearances, and rotation of shaft and coupler (includes removing and reinstalling safety cover). 11. Centrifugal pump: tighten or replace loose, missing or damaged nuts, bolts, or screws. 12. Centrifugal pump: lubricate pump and motor as required. 13. Centrifugal pump: check suction or discharge pressure gauge readings and flow rate. 14. Centrifugal pump: check packing glands and tighten or repack as required; note that slight dripping is required for proper lubrication of shaft. 15. Inspect and clean strainers after each use and flow test. 16. Clean equipment and surrounding area. 17. Complete work order data. Coordinate w/Fire Inspectors. | COMS_FIRE INSPEC
COMS-FP-018S | 1.Clean track 2.Lubricate pulleys. 3.Inspect cable or chain for wear or damage and proper threading through pulleys. 4.Replace fusible links or other heat activated devices that have been painted. Check operation of other heat activated devices. 5.Permanently remove obstructions that prohibit movement of door. 6.Check operation of door by disconnecting or lifting counterweight or other appropriate means. 7.Check fit of door in binders and fit against stay roll. 8.Check door for breaks in covering and examine for dry rot. 9.Clean area around the equipment 10. Complete work order data. | COMS_FIRE INSPEC
COMS-GEV-001A | 1. Check instruments for proper operation 2. Check battery for water level, specific gravity and damage 3. Lubricate chassis 4. Test electric ccable for grounds/shorts 5. Examine drag linkage and steering assembly 6. Check gear case, fill A/R 7. Check wheel bolts and studs 8. Lubricate latches, raisersm, locks, handles 9. Perform complete exterior inspection | COMS_EQUIP MECH
COMS-GEV-001Q | 1. Check instruments for proper operation 2. Check battery for water level, specific gravity, corrosion and damage 3. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-002A | 1. Torque test cylinder head bolts 2. Visually check cylinder head gasket 3. Check body for metal deterioration, squeaks, painting, upholstery, mats, etc. 4. Check frame, hangers, members, etc. 5. Tighten radiator stay bolts and tie rods 6. Check exhaust system connections 7. Check wheel play and bearing 8. Repack wheel bearings and replace tetainer 9. Check instruments for proper operation 10. Check brake pedal travel 11. Inspect fan assembnly, Adjust belts A/R 12. Check for water, oil, fuel or muffler leaks 13. Check battery for water level, specific gravity, corrosion and damage 14. Check fuel filters, strainers and bowl 15. Lubricate chassis 16. Conduct timing test 17. Test electric cable for grounds/shorts 18. Examin drag linkage and steering assembly 19. Check wheel bolts and studs 20. Torque axle flange nuts 21. Inspect tires for wear, inflation and pressur 22. Examine springs and ubolt connections 23. nspect joints and driveline, Repack A/R 24. Check gear case, Fill A/R 25. Lubricate latches, raisers, locks, handles 26. Perform complete exterior inspection 27. Change oil and oil filter 28. Change A filter 29. Lubricate starter, carburetor linkage and distributor shaft | COMS_EQUIP MECH
COMS-GEV-002Q | 1. Check instrumentss for proper operation 2. Check brake pedal ftravel 3. Inspect fan assembly, adjust A/R 4. Check for oil leaks 5. Check battery for water level, specific gravity, corrosion and damage 6. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-002S | 1. Test electric cable for grounds/shorts 2. Examine drag linkage and steering assembly 3. Check wheel bolts and studs 4. Torque axle flange nuts 5. inspect tires for wear, inflation and pressure 6. Examine springs and ubolt connections 7. Inspect joints and driveline, repack A/ 8. Check gear case, fill A/R 9. Lubricate latches, raisers, locks, handles 10. Perform complete exterior inspection 11. Check tire pressure | COMS_EQUIP MECH
COMS-GEV-003A | 1. Test clutch operation, adjust A/R 2. Adjust belts A/R 3. Oil, fuel or exhaust leaks 4. Check fuel filters, strainers 5. Check safety equipment | COMS_EQUIP MECH
COMS-GEV-004A | **NOTE: Maintenance shall be performed in conjunction with Quarterly PM ** 1. Clean and repack trailer axle wheel bearings with a lithium-based bearing grease. 2. Replace the cotter key upon reassembly of wheel bearings. 3. Inpsect the condition of the lining on the brake shoes. 4. Adjust the nylatron wear pads for the mast as necessary to ensure proper operation of mast. 5. Inspect trailer integrity to ensure no rust or cracks in the frame are forming. 6. Replace the backup memory battery on the Control Console using a high-energy lithium battery. Main power switch must be in the ON position to ensure memory is not lost. See O&M Manual for specific battery options. 7. Check firmware for updates, apply as needed. 8. Use onboard Energy Management System Control Unit to check voltage & charge for solar array into battery bank. | COMS_EQUIP MECH
COMS-GEV-004Q | 1. Lubricate pivot points. Apply to rotor plate and dual cam locking mechanism. Use quality lithium grease or chain lube. 2. Lubricate swivel jacks at each corner using quality chain lube on swivel bearings. 3. Lubricate the surge brake actuator. Use a lithium-base lubricant to the zerk fittings on the side of the actuator. 4. Check brake fluid level, add as needed using DOT 3 brake fluid only. 5. Check hydraulic fluid level, add as needed using Dexron II ATF. 6. Inspect sign panel support cradles. 7. Check electrolyte fluid level, add distilled water as needed. 8. Check battery terminals for tightness and corrosion, tighten and clean as required. 9. Check tire pressure, add air as required. 10. Check sign panel for proper operation. 11. Check & clean solar panels as required following O&M recommended procedure. 12. Clean sign display and entire unit following O&M recommended procedure. | COMS_EQUIP MECH
COMS-GEV-005S | 1. Inspect chain and bar for sharpness, wear and damage, repair as needed. 2. Inspect air filter and replace as needed. 3. Inspect fuel lines and repair as needed. 4. Inspect fuel filter and replace as needed. 5. Inspect spark plug and replace as needed. 6. Check and fill bar oiling system. 7. Test chain brake and repair if needed. 8. Fill fuel tank with ethanol free 40:1 mixed fuel 9. Test run and clean saw. 10. Complete work order data. | COMS_EQUIP MECH
COMS-GEV-006A | 1. Torque test cylinder head bolts 2. Visually check cylinder head gasket 3. Check body for metal deterioration, squeaks, painting,upholstery, mats, etc 4. Check frame, hangers, members, etc 5. Tighten radiator stay bolts and tie rods 6. Check exhaust system connections 7. Check wheel play and bearing 8. Repack wheel bearings and replace retainer 9. Tighten body mounting bolts 10. Drain air brake tank, inspect 11. Inspect compressor, hose connection, shut off valve and hydrovac 12. Check fifth wheel mounting lock 13. Perform emission test 14. Check bed hydraulic system | COMS_EQUIP MECH
COMS-GEV-006Q | 1. Check instruments for proper operation 2. Inspect adjust belts A/R 3. Check for oil, fuel or muffler leaks 4. Load test engine performance using water to simulate paint product | COMS_EQUIP MECH
COMS-GEV-007A | 1. Torque test cylinger head bolts 2. Visually check cylinder head gasket 3. Check body for metal deterioration, squeaks, painting, upholstery, mats, etc 4. Check frame, hangers, members, etc 5. Tighten radiator stay bolts and tie rods 6. Check exhaust system connnections 7. Check wheel play and bearing 8. Repack wheel bearings and replace retainer 9. Tighten body mounting bolts 10. Check bed hydraulic system | COMS_EQUIP MECH
COMS-GEV-007Q | 1. Check instruments for proper operation 2. Check brake pedal travel and adjust 3. Check lights 4. Inspect fan assembly, adjust A/R 5. Check for water, oil, fuel or muffler leaks 6. Check battery for water level, specific gravity, corrsion and damage 7. Check fuel filters, strainers and bowl | COMS_EQUIP MECH
COMS-GEV-007S | 1. Test elect4ric cable for grounds/shorts 2. Examine drag linkage and steering assembly 3. Check wheel bolts and studs 4. Inspect tires for wear, inflation and pressure 5. Examin springs and ubolt connections 6. Inspect joints and driveline, repack A/R 7. Check gear case, fill A/R 8. Perform complete exterior inspection 9. Change oil and oil filter 10. Change A filter 11. Lubricate | COMS_EQUIP MECH
COMS-GEV-011A | 1. Test electric cable for grounds/shorts and make repairs 2. Examine drag linkage and steering assembly 3. Gauge check wheel alignment 4. Check wheel bolts and studs 5. Torque axle flange nuts 6. Inspect tires for wear, inflatin and pressure 7. Examine springs and ubolt connections 8. Inspect joints and driveline, repack A/R 9. Lubricate latches, raisers, locks, handles 10. Perform complete exterior inspection 11. Change oil and oil filter 12. Change Air filter 13. Lubricate starter, carburetor linkage and distributor shaft 14. Visually check cylinder head gasket 15. Check body for metal deterioration, squeaks, painting, upholstery, mats, etc 16. Check frame, hangers, members, etc 17. Tighten radiator stay bolts and tie rods 18. Check exhaust system connections 19. Check wheel play and bearing 20. Repack wheel bearings and replace retainer 21 Tighten body mounting bolts | COMS_EQUIP MECH
COMS-GEV-011Q | 1. Check instruments for proper operation 2. Check brake pedal travel 3. Fill master cylinder and adjust brakes 4. Check lights, signals, wipers and mirrors 5. Check radiator hose connections 6. Check thermostat 7, Test antifreeze 8. Inspect fan assembly, adjust belts A/R 9. Check for water, oil, fuel or muffler leaks 10. Check battery for water level, specific gravity, corrosion and damage 11. Check fuel filters, strainers and bowl 12. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-011S | 1. Vacuum at ccarburetor, adjust A/R 2. Conduct timing test 3. Test electric cable for grounds/shorts 4. Examine drag linkage and steering assembly 5. Check wheel bolts and studs 6. Torque axle flange nuts 7. Inspect tires for wear, inflation and pressure 8. Examine springs and ubolt connections 9. Inspect joints and driveline, repack A/R 10. Check gear case, fill A/R 11. Lubricate latches, raisers, locks, handles 12. Perform complete exterior inspection 13. Change oil and oil filter 14. Change A filter 15. Lubricate starter, carburetor linkage and distributor shaft | COMS_EQUIP MECH
COMS-GEV-012A | 1. Torque test cylindr head bolts 2. Visually check cylinder head gasket 3. Check body for metal deterioration, squeaks, painting 4. Check frame, hangers, members, etc 5. Check exhaust system connections 6. Check wheel bearings and replace retainer 8. Tighten body moujnting bolts 9. Check fifth wheel mounting lock 10. Perform emission test | COMS_EQUIP MECH
COMS-GEV-012Q | 1. Check instruments for proper operation 2. Check lights 3. Check for oil, fuel or muffler leaks 4. Check battery for water level, specific gravity, corrosion and damage 5. Check tire pressure 6. Test run | COMS_EQUIP MECH
COMS-GEV-012S | 1. Vacum at carburetor, adjust A/R 2. Conduct timing test 3. Test electric cable for grounds/shorts 4. Examine drag linkage and steering assembly 5. Check wheel bolts and studs 6. Inspect tires for wear, inflation and pressure 7. Examine springs and ubolt connections 8. Lubricate latches, raisers, locks and handles 9. Perform complete exterior inspection 10. Change oil 11. Change A filter 12. Lubricate carburetor linkage | COMS_EQUIP MECH
COMS-GEV-013A | 1. Torque test cylinder head bolts 2. Visually check cylinder head gasket 3. Check body for metal deterioration, squeaks, painting 4. Check frame, hangers, members, etc 5, Check exhaust system connections 6. Perform emission test | COMS_EQUIP MECH
COMS-GEV-013Q | 1. Check for oil, fuel or muffler leaks 2. Check battery for water level, specific gravity, corrosion and damage 3. Check strainers | COMS_EQUIP MECH
COMS-GEV-013S | 1. Vacuum at carburetor, adjust A/R 2. Conduct timing test 3. Test electric cable for gounds/shorts 4. Perform emission test 5. Change oil and oil filter 6. Change A filter 7. Lubricate starter, carburetor linkage and distributor shaft | COMS_EQUIP MECH
COMS-GEV-015A | 1. Check instruments for proper operation 2. Check radiator hose connectins 3. Check thermostat 4. Test antifreeze 5. Inspect fan assembly, adjust belts A/R 6. Check for water, fuel, oil or muffler leaks 7. Check battry for water level, specific gravity, corrosion and damage 8. Check fuel filters, strainers and bowl 9. Test electric ccable for grounds/shorts 10. Check wheel bolts and studs 11. Inspect tires for wear, inflation and pressure 12. Examine ubolt connections 13. Lubricate latches, raiser, locks and handles 14. Perform complete exterior inspection 15. Change oil and oil filter 16. Change A filter 17. Visually check cylinder head gasket, squeks, painting 18. Check frame, hangers, members etc 19. Tighten radiator stay bolts and tie rods 20. Check exhaust system connections 21. Repack wheel bearings and replace retainer | COMS_EQUIP MECH
COMS-GEV-015Q | 1. Check instruments for proper operation 2. Check radiator hose connections 3. Check thermostat 4. Test antifreeze 5. Inspect fan assembly, adjust belts A/R 6. Check for water, fuel, oil or muffler leaks 7. Check battery for water level, specific gravity, corrosion and damage 8. Check fuel filters, strainers and bowl 9. Test run 10. Check tire psi | COMS_EQUIP MECH
COMS-GEV-015S | 1. Test electric cable for grounds/shorts 2. Check wheel bolts and studs 3. Inspect tires for wear, inflation and pressure 4. Examine ubolt connections 5. Lubricate latches, raisers, locks and handles 6. Perform complete exterior inspection 7. Change oil and oil filter 8. Change A filter | COMS_EQUIP MECH
COMS-GEV-017A | 1. Vacuum at carburator , adjust A/R 2. Conduct timing test 3. Test electric cable for grounds/shorts 4. jCheck wheel bolts and studs 5. Torque axle flange nuts 6. Inspect tires for wear, inflation and pressure 7. Examine springs and ubolt connections 8. Perform complete exterior inspection 9. Lubricate latches, raisers, locks, handles 10. Change oil and oil filter 11. Change A filter 12. Lubricate carburetor linkage 13. Torque test cylinder head bolts 14. Visually check cylinder head gasket 15. Check body for metal deterioration, squeaks, paintins 16. Check frame, hangers, members, etc 17. Check exhaust system connections 18. Check wheel berings and replace retainers 19. Check wheel play and bearing 20. Tighten body mounting bolts 21. Inspect compressor, hose connection, shut off valve 22. Check fifth wheeel mounting lock | COMS_EQUIP MECH
COMS-GEV-017Q | 1. Check instruments for proper operation 2. Check for water, oil, fuel or muffler leaks 3. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-018A | 1. Vacuum at carburetor, adjust A/R 2. Conduct timing tet 3. Test electric cable for gounds/shorts 4. Examine drag linkage and steering assembly 5. Check wheel bolts and studs 6. Inspect tires for wear, inflation and pressure 7. Examine springs and ubolt connections 8. Lubricate latches, raisers, locks, handles 9. Perform complete exterior inspection 10. Change oil and oil filter 11. Service air filter 12. Lubricate, carburetor linkage 13. Torque test cylinder head bolts 14. Visully check cylinder head gasket 15. Check bodty for metal deterioration, squeaks, painting 16. Check frame, hangers, members, etc 17. Tighten radiator stay bolts and tie rods 18. Check exhaust system connections 19. Repack wheel bearings and replace retainers 20. Test antifreeze | COMS_EQUIP MECH
COMS-GEV-018Q | 1. Check instruments for proper operation 2. Adjust brakes 3. Check radiator hose connections 4. Check thermostat 5. Test antifreeze 6. Inspect rfan assembly, Adjust belts A/R 7. Check for water, oil, fuel or muffler leaks 8. Check battery for water level, specific gravity, corrosion and damage 9. Check fuel filters, strianer and bowl 10. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-019A | 1. Check instruments for proper operation 2. Check for water, fuel, oil or muffler leaks 3. Change pressure pump oil 4. Test electric cable for grounds/shorts 5. Perform complete exterior inspection 6. Change oil 7. Lubricate carburetor linkage 8. Torque test cylinder head bolts 9. Visually check cylinder head gasket 10. Check exhaust system connections 11. Change foam air filter and prefilter 12. Inspect fuel lines for cracks and brittleness 13. Add fuel treatment to the fuel system | COMS_EQUIP MECH
COMS-GEV-021A | 1. Test electric cables for grounds/shorts 2. Examine drag linkage and steering assembly 3. Gauge check wheel alignment 4. Check wheel bolts and studs 5. Torque axle flange nuts 6. Inspect tires for wear, inflation and pressure 7. Examine springs and ubolt connections 8. Inspec joints and driveline, repack A/R 9. Lubricate latches, raisers, locks, handles 10.Perform complete exterior inspecton 11. Change oil and oil filter | COMS_EQUIP MECH
COMS-GEV-021Q | 1. Check instruments for proper operation 2. Check brake pedal travel 3. Fill master cylineder and adjust brakes 4. Test clutch operation, adjust A/R 5. Check lights, signals, wipers and mirrors 6. Check radiator hose connections 7. Check thermostat 8. Test antifreeze 9. Inspec tan assembly, adjust belts A/R 10. Check for water, oil, fuel or muffler leaks 11. Check battery for water level, specific gravity, corrosion and damage 12. Check fuel filters, strainers and bowl 13. Check safety equipent, flares, extinguishers 14. Lubricat chassis | COMS_EQUIP MECH
COMS-GEV-024A | 1. Vacuum at carburetor, adjust A/R 2. Test electric cable for grounds/shorts 3. Check wheel bolts and studs 4. Inspect tires for wear, inflation and pressure 5. Lubricate latches, raisers, locks, handles 6. Perform complete exterior inspection 7. Change oil 8. Change filter 9. Lubricate carburetor linkage | COMS_EQUIP MECH
COMS-GEV-024Q | 1. Check instruments for proper operation 2. Test clutch operation, adjust A/R 3. Check for water, oil, fuel or muffler leaks 4. Check fuel filters, strainers and bowl 5. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-025Q | 1. Check instruments for proper operation 2. Check brake pedal travel 3. Fill master cylinder and adjust brakes 4. Test clutch operation, Adjust A/R 5. Check ligthts, signals, wipers and mirrors 6. Check radiator hose connections 7. Check thermostat 8. Test antifreeze 9. Inspect fan assembly, adjust belts A/R 10. Check for water, oil, fuel or muffler leaks 11. Check battery for water level, specific gravity, corrosion and damage 12. Check fuel filters, strainers and bowl 13. Check safety equipment, flares and extinguishers 14. Lubricate chassis | COMS_EQUIP MECH
COMS-GEV-025S | 1.Test electric cable for grounds/shorts 2. Examine drag linkage and steering assembly 3.Gauge check wheel alignment 4. Check wheel bolts and studs 5. Torque axle flange nuts 6. Inspect tires for wear, inflation and pressure 7. Examine springts and ubolt connections 8. Inspect joints and driveline, repack A/R 9. Check gear case, fill A/R 10. Lubricate latches, raisers, locks and handles 11. Perform complete exterior inspection 12. Change oil and oil filter | COMS_EQUIP MECH
COMS-GEV-026A | 1. Check instruments for proper operation 2. Test cluch operation, adjust A/R 3. Inspec fan assembly, adjust belt A/R 4 Check for water, oil, fuel or muffler leaks 5. Check fuel filters, strainers and bowl 6. Lubricate chassis 7. Test electric cable for grounds/shorts 8. Gauge check wheel alignment 9. Check wheel bolts and studs 10. Torque axle flange nuts 11. Inpsect tires for wear, inflation and pressure 12. Examin springs and ubolt connections 13. Inspect joints nad driveline, repack A/R 14. Check gear case, fill A/R 15. Lubricate latches, raisers, locks, handles 16. Perform complete exterior inspection 17. Change oil and oil filter 18. Change A filter 19. Rotate tires | COMS_EQUIP MECH
COMS-GEV-029A | 1. Check hydraulic oil reservoir 2. Test battery cable for grounds/shorts 3. Check wheel bolts and studs 4. Inspect tires for wear and pressure 5. Inspect suspension if applicable. 6. Inspect joints and driveline. Repack as required 7. Check gear case, fill as required 8. Lubricate latches, raisers, locks, handles 9. Perform complete exterior inspection 10. Change hydraulic oil filter | COMS_EQUIP MECH
COMS-GEV-029Q | 1.Check instruments for proper operation 2. Check lights, and AC work outlets 3. Check reservoir for hydraulic oil 4. Check battery for water level, specific gravity, corrosion and damage 5. Check safety equipment, flares, extinguisher 6. Lubricate chassis 7. Check battery charger | COMS_EQUIP MECH
COMS-GEV-029S | 1. Check body for metal deterioration, squeaks, painting 2. Check frame, hangers, members, etc 3. Check wheel play and bearing 4. Tighten body mounting bolts 5. Check bed hydraulic system | COMS_EQUIP MECH
COMS-GEV-031A | 1. Check wheel bolts and studs 2. Torque axle flange nuts 3. Inspect tires for wear, inflation and pressure 4. Examine springs and ubolt connections 5. Lubricate, latches, raisers, locks, handles 6. Perform complete exterior inspection 7. Check body for metal deterioration, squeaks, painting 8. Check frame, hangers, members, etc 9. Repacck wheel bearings and replace retainers 10. Tighten body mounting bolts | COMS_EQUIP MECH
COMS-GEV-035S | 1. Test electric cable for grounds/shorts and high resistance loads. 2. Examine drag linkage and steering assembly. 3. Tighten axle flange nuts. 4. Inspect tires for wear,inflation and pressure. Adjust to proper pressure as needed. 5. Examine springs and ubolt connections. 6. Lubricate latches, raisers, locks, handles and chassis 7. Perform complete exterior inspection for corrosion including body hangars and members and ensure all exterior components are secure. 8. Inspect windshield wiper blades for wear, replace as needed, and fill wiper fluid tank. 9. Check wheel play, bolts,studs, repack wheel bearings and replace retainers. 10. Tighten body mounting bolt. 11.Check instruments for proper operation 12. Check brakes,brake pedal travel and master cylinder fluid level, perform necessary adjustments and fill fluid level as needed. 13.Inspect batteries for corrosion and damage. Clean corroded area as needed and check battery charger for proper operation. 14. Inspect all vehicle safety equipment,extinguishers, seat belts etc.. 15.Check motor case oil level fill as needed | COMS_EQUIP MECH
COMS-GEV-100A | **Note: Annual PM must be performed in conjunction with Monthly and Semiannual PM 1. Replace fuel filter(s). 2. Clean all fuel traps. 3. Clean and inspect fuel injectors. 4. Replace coolant filter(s). 5. Check and record concentration and pH level of coolant. 6. Replace air filter(s). 7. Check combustion air cleaner. 8. Inspect and clean positive crankcase vent system filter and components. 9. Inspect generator bearings and lubricate. 10. Inspect generator for misalignment with engine. 11. Inspect generator terminals for condition and tighten as needed. 12. Check control panel for condition of relays, terminals, contacts and insulation. Ensure relays and terminals are tight. Clean device contacts. 13. Inspect all transfer swtiches. 14. Apply anti-corrosion grease to all battery terminals. 15. Check all hoses and fittings for condition and tightness. 16. Perform generator load test for a minimum of one (1) hour. 17. Log all readings: Oil Pressure, Oil Temperature, Coolant Temperature, Output Frequency, Output Voltage, Output Current, etc. 18. Inspect head gasket thoroughly for leaks or failure. 19. Check condition of exciter operation. 20. Inspect and clean load bank. 21. Lubricate all handles, latches, doors, hinges, etc. | COMS_EQUIP MECH
COMS-GEV-100B | **Note: Biennial PM must be performed in conjunction with Monthly, Semiannual, and Annual PM 1. Replace engine oil. 2. Replace engine oil filter(s). | COMS_EQUIP MECH
COMS-GEV-100M | 1. Check with operating or building personnel for any known deficiencies. 2. Record hours before starting generator. 3. Place controls in the 'OFF' position. 4. Check to ensure there is a sufficient amount of fuel in the fuel tank. Tank should not be less than half full. 5. Check and record engine oil level. Add oil to required level if necessary. 6. Check and record coolant level. Coolant should be visible at the top of the radiator. Record non-running coolant temperature. 7. Check and clean area to ensure there are not any obstructions to flow of cooling air. 8. Check engine heater operation. For circulating systems, ensure flow is present. 9. Inspect starting batteries for damage, bulging, cracks, and corrosion. 10. Check electrolyte level in all batteries and add if necessary. 11. Check battery connections for corrosion and tighten as needed. Record static and cranking battery voltage. 12. Check battery charger operation and charge rate. 13. Check for any oil, fuel, exhaust, and/or coolant leaks. Check for oil/exhaust leaks around turbocharger(s). 14. Inspect fan blades for cracks or loose blades. 15. Check fan belt condition and tension, adjust as needed. 16. Check for broken and loose wires. 17. Check exhaust system. System must be clear and rain cap unobstructed. Check for rust. 18. Press test lamp buttons to ensure all test lamps are functioning properly. 19. Exercise unit for 30 minutes. Unit should be started under zero load and load slowly added once engine is at operating temperature. 20. Log all readings: Oil Pressure, Oil Temperature, Coolant Temperature, Output Voltage, Output Current, Output Frequency, etc. 21. Inspect and check operation of day tank and fuel supply. Ensure all indicators and alarms are working properly. 22. Inspect all automatic transfer switches. 23. Return controls to 'AUTO' position. 24. Record hours after PM completion. 25. Clean unit and surrounding area. | COMS_EQUIP MECH
COMS-GEV-100S | **Note: Semiannual PM must be performed in conjunction with Monthly PM. 1. Check condition and concentration of coolant. 2. Check all coolant hoses for potential failure and tighten all clamps. 3. Clean air filters. Perform air inlet restriction test. 4. Inspect and adjust belts and linkages as needed. 5. Inspect fuel system, including injection system, fuel lines, and any fuel strainers. Clean out all fuel strainers. 6. Check and record specific gravity of all batteries. 7. Check all engine and generator shutdown, alarm, and safety systems. 8. Adjust output voltage and frequency as required. 9. Confirm proper operation of all engine gauges and AC metering. 10. Check turbocharger for operation and excess noise. | COMS_EQUIP MECH
COMS-GEV-101A | 1. Check with operating or area personnel for deficiencies. 2. Inspect wiring, wiring connections, and fuse blocks for looseness, charring, evidence of short circuiting, overheating and tighten all connections. 3. Inspect general condition of transfer switch and clean exterior and surrounding area. 4. Provide one week notification to COR prior to performing work. 5. Provide a 120/208V 3p generator and associated cables capable of supporting an 80kW load. 6. Install generator to the manual transfer switch tap box. 7. Prestart the generator, verifying emergency source availability at the manual transfer switch. 8. Transfer the Secure Room to the neutral position and allow battery source to maintain power to the room rack equipment and confirm that there is no UPS loads shutdown. 9. Complete the transfer to the generator source and run for 1 hour. 10. Verify normal source is available and transfer the secure room back to normal power. | COMS_EQUIP MECH
COMS-GEV-200A | **Note: Annual PM must be performed in conjunction with Monthly and Semiannual PM 1. Replace fuel filter(s). 2. Clean all fuel traps. 3. Clean and inspect fuel injectors. 4. Replace coolant filter(s). 5. Check and record concentration and pH level of coolant. 6. Replace air filter(s). 7. Check combustion air cleaner. 8. Inspect and clean positive crankcase vent system filter and components. 9. Inspect geneator bearings and lubricate. 10. Inspect generator for misalignment with engine. 11. Inspect geneator terminals for condition and tighten as needed. 12. Check all hoses and fittings for condition and tightness. 13. Check control panel for condition of relays, terminals, contacts and insulation. Ensure relays and terminals are tight. Clean device contacts. 14. Apply anti-corrosion grease to all battery terminals. 15. Inspect all transfer swtiches. 16. Perform generator load test for a minimum of one (1) hour. 17. Log all readings: Oil Pressure, Oil Temperature, Coolant Temperature, Output Frequency, Output Voltage, Output Current, etc. 18. Inspect head gasket thoroughly for leaks or failure. 19. Lubricate all handles, latches, doors, hinges, etc. 20. Check condition of exciter operation. 21. Lubricate all handles, latches, doors, hinges, etc. | COMS_EQUIP MECH
COMS-GEV-200B | **Note: Biennial PM must be performed in conjunction with Monthly, Semiannual, and Annual PM 1. Replace engine oil. 2. Replace engine oil filter(s). | COMS_EQUIP MECH
COMS-GEV-200M | 1. Check with operating personnel for any known deficiencies. 2. Record unit hours before starting generator. 3. Check to ensure there is a sufficient amount of fuel in the fuel tank. Tank should be at least half full. 4. Check and record engine oil level. Add oil to required level if necessary. 5. Check and record coolant level. Coolant should be visible at the top of the radiator. Record non-running coolant temperature. 6. Ensure there are not any obstructions causing air flow obstruction to flow of cooling air. 7. Check engine heater operation. For circulating systems, ensure flow is present. 8. Inspect starting batteries for damage, bulging, cracks, and corrosion. 9. Check electrolyte level in all batteries and add if necessary. 10. Check battery connections for corrosion and tighten as needed. Record static and cranking battery voltage. 11. Check battery charger operation and charge rate. 12. Check for any oil, fuel, exhaust, and coolant leaks. Check for oil/exhaust leaks around turbocharger(s). 13. Inspect fan blades for cracks or loose blades. 14. Check fan belt condition and tension, adjust as needed. 15. Check for broken and loose wires. 16. Check exhaust system. System must be clear and rain cap unobstructed. Check for rust. 17. Press test lamp buttons to ensure all test lamps are functioning properly. 18. Exercise unit for 30 minutes. Unit should be started under zero load and load slowly added once engine is at operating temperature. Utilize portable load bank for load testing. 19. Log all readings: Oil Pressure, Oil Temperature, Coolant Temperature, Output Voltage, Output Current, Output Frequency, etc. 20. Record unit hours after PM completion. 21. Clean unit and surrounding area. | COMS_EQUIP MECH
COMS-GEV-200S | **Note: Semiannual PM must be performed in conjunction with Monthly PM. 1. Check condition and concentration of coolant. 2. Check all coolant hoses for potential failure and tighten all clamps. 3. Clean air filter(s). Perform air inlet restriction test. 4. Inspect and adjust belts and linkages as needed. 5. Inspect fuel system, including injection system, fuel lines, and any fuel strainers. Clean out all fuel strainers. 6. Check and record specific gravity of all batteries. 7. Check all engine and generator shutdown, alarm, and safety systems. 8. Adjust output voltage and frequency as required. 9. Confirm proper operation of all engine gauges and AC metering. 10. Check turbocharger for operation and excess noise. 11. Inspect unit wheels, tires, drag linkage, and steering assembly (if applicable). Ensure tires are properly inflated. | COMS_EQUIP MECH
COMS-GEV-300A | **Note: Annual PM must be performed in conjunction with Monthly and Semiannual PM 1. Replace natural gas filter(s). 2. Clean and inspect fuel injectors. 3. Replace coolant filter(s). 4. Check and record concentration and pH level of coolant. 5. Replace air filter(s). 6. Check combustion air cleaner. 7. Inspect and clean positive crankcase vent system filter and components. 8. Inspect, clean, and gap spark plugs to manufacturer's specifications. 9. Inspect spark plug wires, ignition coil wire, and boots. 10. Check control panel for condition of relays, terminals, contacts and insulation. Ensure relays and terminals are tight. Clean device contacts. 11. Inspect generator bearings and lubricate. 12. Inspect generator for misalignment with engine. 13. Inspect generator terminals for condition and tighten as needed. 14. Apply anti-corrosion grease to all battery terminals. 15. Check all hoses and fittings for condition and tightness. 16. Check natural gas system parameters and record: Primary pressure regulator output pressure, secondary pressure regulator output pressure @ no load and max load. 17. Inspect all transfer swtiches 18. Perform generator load test for a minimum of one (1) hour. 19. Log all readings: Oil Pressure, Oil Temperature, Coolant Temperature, Output Frequency, Output Voltage, Output Current, etc. 20. Inspect head gasket thoroughly for leaks or failure. 21. Check condition of exciter operation. 22. Inspect and clean load bank. 23. Lubricate all handles, latches, doors, hinges, etc. | COMS_EQUIP MECH
COMS-GEV-300B | **Note: Biennial PM must be performed in conjunction with Monthly, Semiannual, and Annual PM 1. Replace engine oil. 2. Replace engine oil filter(s). | COMS_EQUIP MECH
COMS-GEV-300M | 1. Check with operating or building personnel for any known deficiencies. 2. Record unit hours before starting generator. 3. Place controls to the 'OFF' position. 4. Check and record engine oil level. Add oil to required level if necessary. 5. Check and record coolant level. Coolant should be visible at the top of the radiator. Record non-running coolant temperature. 6. Check and clean area to ensure there are not any obstructions to flow of cooling air. 7. Check engine heater operation. For circulating systems, ensure flow is present. 8. Inspect starting batteries for damage, bulging, cracks, and corrosion. 9. Check electrolyte level in all batteries and add if necessary. 10. Check battery connections for corrosion and tighten as needed. Record static and cranking battery voltage. 11. Check battery charger operation and charge rate. 12. Check for any oil, gas, exhaust, and coolant leaks. Check for oil/exhaust leaks around turbocharger(s). 13. Inspect fan blades for cracks or loose blades. 14. Check fan belt condition and tension, adjust as needed. 15. Check for broken and loose wires. 16. Check exhaust system. System must be clear and rain cap unobstructed. Check for rust. 17. Press test lamp buttons to ensure all test lamps are functioning properly. 18. Exercise unit for 30 minutes. Unit should be started under zero load and load slowly added once engine is at operating temperature. 19. Log all readings: OilPressure, Oil Temperature, Coolant Temperature, Output Voltage, Output Current, Output Frequency, etc. 20. Inspect all automatic transfer switches. 21. Return controls to 'AUTO' position. 22. Record unit hours after PM completion. 23. Clean unit and surrounding area. | COMS_EQUIP MECH
COMS-GEV-300S | **Note: Semiannual PM must be performed in conjunction with Monthly PM 1. Check condition and concentration of coolant. 2. Check all coolant hoses for potential failure and tighten all clamps. 3. Clean air filters. Perform air inlet restriction test. 4. Inspect and adjust belts and linkages as needed. 5. Inspect natural gas lines. Ensure proper pressure is delievered to unit. 6. Check and record specific gravity of all batteries. 7. Check all engine and generator shutdown, alarm, and safety systems. 8. Remove and analyze spark plugs. Reinstall. 9. Adjust output voltage and frequency as required. 10. Confirm proper operation of all engine gauges and AC metering. 11. Check turbocharger for operation and excess noise. | COMS_EQUIP MECH
COMS-GEV-500A | **Note: Annual PM must be performed in conjunction with Semiannual PM. **Note: Steps 1-6 must be completed PRIOR to performing Semiannual PM. 1. Check with operating personel for any deficiencies. 2. Clean air filter with warm, soapy water; reoil. 3. Change engine oil. 4. Clean spark plug with wire brush. 5. Verify spark plug gap is within manufacturer's specifications, and reinstall. 6. Inspect generator bearings and lubricate. 7. Treat fuel system with fuel stabilizer/fuel treatment. 8. Clean unit. | COMS_EQUIP MECH
COMS-GEV-500S | 1. Check engine oil level. 2. Ensure generator has a sufficient amount of fuel prior to starting. 3. Check for any oil, fuel, or exhaust leaks. 4. Check all hoses, clamps, and fittings for condition and tightness. 5. Run generator for 20 minutes under load to ensure proper operation. Utilize portable load bank to load generator to appropriate level. 6. Check and adjust idle speed. 7. Allow treated fuel to enter carburetor prior to shutting down. Shut fuel off to carburetor if valve installed. 8. Log generator hours in craftsperson notes. 9. Complete work order data | COMS_EQUIP MECH
COMS-HVACR-001S | 1. Stop and start fan with local switch. 2. Check motor and fan shaft bearings for noise, vibration. 3. Lubricate bearings. 4. Check belts for wear, tension and alignment, if applicable. 5. Adjust belts or replace as required. 6. Inspect VFD enclosure and clean, if applicable. 7. Check blower intake dampers, lubricate; if applicable. 8. Check electrical wiring and connections: tighten loose connections. 9. Clean fan and surrounding area. 10. Complete work order data | COMS_HVAC MECH
COMS-HVACR-003A | **Annual PM must be completed in conjuction with Monthly and Quarterly PMs** 1. Check combustion chamber for air or gas leaks. 2. Inspect and clean oil burner. 3. Inspect fuel system for leaks and change fuel filter element, if applicable. 4. Check electrical wiring and connections. 5. Clean firebox. 6. Check boiler operation through complete cycle. 7. Complete work order data | COMS_HVAC MECH
COMS-HVACR-003M | **Quarterly PM must be completed in conjuction with Monthly PM** 1. Inspect fuel lines and connections for damage, if applicable. 2. Check main flame failure protection and flame detection scanners, if applicable. 3. Check operation of control switches including hot water temperature limit and combustion air proving. 4. Check condition of safety relief valve. 5. Check operation of boiler low water cut off devices. 6. Check indicator lights, sight glasses and pressure gauges. 7. Clean area around boiler. 8. Complete work order data | COMS_HVAC MECH
COMS-HVACR-003Q | 1. Check for proper operational response of burner to controls. 2. Check and lubricate burner, blowers and motors as required. 3. Check condition of flue pipe, damper and exhaust stack. 4. Complete work order data | COMS_HVAC MECH
COMS-HVACR-006S | 1. Check with operating or area personnel for deficiencies. 2. Check operation of unit for water leaks, noise and vibration. 3. Clean and inspect hot water basin. 4. Check electrical wiring and connections and adjust as reuired. 5. Lubricate motor and fan bearings. 6. Check fan blades or blower for imbalance and tip clearance. 7. Check belts for wear, tensiona dn alignment; adjust as required. 8. Drain and flush cold water sump and clean strainer. 9. Brush clean inside of tower and remove scale build-up with appropriate compound. 10. Refill with water and check make-uppiping for leakage; repair as required. 11. Inspect and clean around cooling tower. 12. Condition assessment of structure (enter into Craftsperson's notes) 13. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-008S | 1. Check with operating personnel for deficiencies. 2. Clean pump exterior and check for corrosion on pump exterior. 3. Check for leaks on suction and discharge piping. 4. Check pump and motor operation for vibration and noise. 5. Check motor and pump alignment, if applicable and adjust as necessary. 6. Lubricate pump and motor as required. 7. Check pressure gauge readings and flow rates if available. 8. Clean area around pump. 9. Complete work order data | COMS_PLUMBER
COMS-HVACR-011M | 1. Check with operating or area personnel for deficiencies. 2. Check sensor panel for proper operation. 3. Check wiring and electrical connections. 4. Test visual and audible alarm for proper operation. 5. Complete work order data. | COMS_CUP OPER
COMS-HVACR-012A | **Annual PM must be completed in conjuction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan and condensate drain as required. 3. Clean blower and motor as required. 4. Check electrical connections. 5. Check operation and clean dampers, louvers and shutters; lubricate as required. 6. Check filters, replace if needed. 7. Check belts, replace or adjust as needed, where applicable. 8. Apply biocide. 9. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-012Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. Adjust or replace belts as required. 6. Inspect exterior piping and valves for leaks. Inspect coils for debris. 7. Check refrigerant pressure. Add or remove refrigerant, as required. 8. Tighten connections as required. 9. Replace air filters. 10. Clean area around unit. 11. Complete work order data | COMS_HVAC MECH
COMS-HVACR-013A | **Annual PM must be completed in conjuction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan and condensate drain as required. 3. Clean blower and motor as required. 4. Check electrical connections. 5. Inspect VFD enclosure and clean, if applicable. 6. Check operation and clean dampers, louvers and shutters; lubricate as required. 7. Apply biocide. 8. Complete this in conjunction with the Quarterly PM. 9. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-013Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment, where applicable. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks, where applicable. 8. Check refrigerant pressure. Add or remove refrigerant, as required. 9. Tighten connections as required. 10. Replace air filters. 11. Inspect, clean and adjust electrodes and nozzles on oil burners, where applicable. 12. Lubricate control valves and thermo-sensing bulbs on gas burners, where applicable. 13. Oil the burner motor bearings as applicable. 14. Inspect fuel system for leaks. 15. Inspect flame sensor for soot build-up and clean. 16. Change fuel filter element on oil burner, where applicable. 17. Check for proper operation of burner primary controls, check and adjust thermostat. 18. Check condition of flue pipe, damper and stack. 20. Check and clean condensate drain piping. 21. Clean area around unit. 22. Fill out maintenance checklist and report deficiencies. 23. Complete work order data | COMS_HVAC MECH
COMS-HVACR-014A | **Annual PM must be completed in conjuction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan and condensate drain as required. 3. Clean blower and motor as required. 4. Check electrical connections. 5. Inspect VFD enclosure and clean, if applicable. 6. Check operation and clean dampers, louvers and shutters; lubricate as required. 7. Check filters, replace if needed. 8. Check belts, replace or adjust as needed, where applicable. 9. Apply biocide. 10. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-014Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. Adjust or replace belts as required. 6. Inspect exterior piping and valves for leaks. Inspect coils for debris. 7. Check refrigerant pressure. Add or remove refrigerant, as required. 8. Tighten connections as required. 9. Replace air filters. 10. Clean area around unit. 11. Complete work order data | COMS_HVAC MECH
COMS-HVACR-016A | **Annula PM must be completed in conjunction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan and condensate drain as required. 3. Clean blower and motor as required. 4. Check electrical connections, tighten as required. 5. Check compressor oil level; add oil as required. 6. Complete work order data | COMS_HVAC MECH
COMS-HVACR-016Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Perform operational check of unit. 8. Check refrigerant pressure. 9. Add or remove refrigerant, as required. 10. Adjust controls and cycle the reverse cycle valve to insure proper operation. 11. Replace air filters. 12. Clean area around unit. 13. Complete work order data | COMS_HVAC MECH
COMS-HVACR-017S | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check electrical wiring and connections. 6. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 7. Clean drain pan and blower as required. 8. Check belts for wear, proper tension, and alignment; adjust as necessary. 9. Perform operational check of unit. 10. Check refrigerant pressure. 11. Add or remove refrigerant, as required. 12. Clean or replace air filter, as applicable. 13. Clean area around unit. 14. Complete work order data | COMS_HVAC MECH
COMS-HVACR-018A | **Note: Annual PM must be performed in conjunction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Check electrical connections, tighten as required. 3. Check compressor oil level; add oil as required. 4. Complete work order data | COMS_HVAC MECH
COMS-HVACR-018Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Perform operational check of unit. 8. Check refrigerant pressure. 9. Add or remove refrigerant, as required. 10. Inspect fas(s) or blower(s) for imbalance; adjust as required. 11. Clean equipment and surrounding area 12. Complete work order data | COMS_HVAC MECH
COMS-HVACR-019Q | 1. Check with operating personnel for deficiences. 2. Run microprocessor check, if applicable. 3. Check controls and unit for proper operation. 4. Check for unusual noise or vibration. 5. Replace air filters. 6. Lubricate shaft and motor bearings. 7. Check belts for wear, proper tension, and alignment; adjust as necessary. 8. Check humidifier, if applicable. 9. Check humidity lamp or canister, if applicable; replace if necessary. 10. Inspect exterior piping and valves for leaks. 11. Tighten connections as required. 12. Clean area around unit. 13. Complete work order data | COMS_HVAC MECH
COMS-HVACR-019S | 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan blower, motor and drain piping as required. 3. Clean humidifier pan, if applicable. 4. Check operation of unit. 5. Check refrigerant pressure, if applicable; add refrigerant as required. 6. Clean area around unit. 7. Add biocide. 8. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-020A | **Note: Annual PM must be performed in conjunction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Check electrical connections, tighten as required. 3. Complete work order data | COMS_HVAC MECH
COMS-HVACR-020Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Inspect fan(s) or blower(s) for imbalance; adjust as required. 8. Clean area around unit. 9. Complete work order data | COMS_HVAC MECH
COMS-HVACR-022A | 1. Check with operating personnel for deficiencies. 2. Inspect, clean and adjust control valves and thermostat. 3. Inspect coils, connections and piping for leaks. 4. Check fan and motor for vibration and noise. 5. Check electrical wiring to motor. 6. Change air filter(s). 7. Check unit heater operation. 8. Clean area around the heater. 9. Complete work order data | COMS_HVAC MECH
COMS-HVACR-023A | 1. Check with operating personnel for deficiencies. 2. Check blower and motor for vibration and noise. 3. Check belts for proper tension , tightened as required. 4. Change air filter(s). 5. Check unit heater operation. 6. Check electrical connections and tighten as required. 7. Clean area around the heater. 8. Complete work order data | COMS_HVAC MECH
COMS-HVACR-024A | 1. Inspect, clean and adjust electrodes, fuel filter and nozzles on oil burners if applicable. 2. Inspect, clean and adjust control valves and thermo-sensing bulbs on gas burners if applicable. 3. Lubricate oil burner motor bearings as applicable. 4. Check electrical connections and tighten as required. 5. Inspect ancd clean firebox. 6. Check condition of flue pipe, damper and stack. 7. Clean area around the heater. 8. Complete work order data | COMS_HVAC MECH
COMS-HVACR-024Q | 1. Check with operating personnel for deficiencies. 2. Inspect fuel system for leaks. 3. Check for proper operation of burner primary controls. 4. Check blower and motor for vibration and noise. 5. Check belts for proper tension , tightened as required. 6. Check operation. 7. Clean area around the heater. 8. Complete work order data | COMS_HVAC MECH
COMS-HVACR-026A | 1. Check baseboard during operating season. 2. Check hot water piping and control valves for leaks. 3. Check electric baseboard electrical connections. 4. Check controls for proper operation. 5. Complete work order data | COMS_HVAC MECH
COMS-HVACR-027S | 1. Operate humidistat through its throttling range to verify operation. 2. Inspect steam trap, if applicable. 3. Clean strainer, if applicable. 4. Clean and/or replace water/steam nozzles as necessary. 5. Inspect controls. 6. Inspect steam/water lines for leaks and corrosion, repair as required. 7. Complete work order data | COMS_HVAC MECH
COMS-HVACR-029Q | 1. Check with operating personnel for deficiencies. 2. Clean compressor air filter 3. Check drive belts for condition and tension. 4. Change compressor oil. 5. Clean air dryer and surrounding area. 6. Complete work order data | COMS_HVAC MECH
COMS-HVACR-029S | 1. Inspect pipng system for leaks and repair as required. 2. Test air dryer for refrigerant leaks. 3. Inspect foundation fasteners. 4. Complete work order data | COMS_HVAC MECH
COMS-HVACR-030Q | 1. Check with operating personnel for deficiencies. 2. Verify air flow across booth. 3. Replace filters as required. 4. Complete work order data | COMS_HVAC MECH
COMS-HVACR-031Q | 1. Check with operating personnel for deficiencies. 2. Verify air flow through system. 3. Clean or replace filter media as required. 4. Check controls and verify operation. 5. Complete work order data | COMS_HVAC MECH
COMS-HVACR-032Q | 1. Replace air filters. 2. Complete work order data | COMS_HVAC MECH
COMS-HVACR-032S | 1. Stop and start fan with local switch. 2. Check motor and fan shaft bearings for noise, vibration. 3. Lubricate bearings. 4. Check belts for wear, tension and alignment, if applicable. 5. Adjust belts or replace as required. 6. Check blower intake dampers, lubricate; if applicable. 7. Check electrical wiring and connections: tighten loose connections. 8. Clean fan and surrounding area. 9. Complete work order data | COMS_HVAC MECH
COMS-HVACR-033A | 1. Check operating performance. 2. Clean or replace filters as required, if applicable. 3. Check controls. 4. Check electrical wiring and connections; adjust as required. 5. Lubricae blower and motor bearings. 6. Clean the equipment and the surrounding area. 7. Complete work order data | COMS_HVAC MECH
COMS-HVACR-036Q | 1. Check with operating personnel for deficiencies. 2. Check controls and gauges if applicable. 3. Replace air filters. 4. Clean area around unit. 5. Complete work order data | COMS_HVAC MECH
COMS-HVACR-039S | 1. Check damper motor for proper operation. 2. Adjust damper linkage if necessary. 3. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-044Q | 1. Check with operating or area personnel for any deficiencies. 2. Remove and install access panel. 3. Lubricate all moving parts, pivot points and fan motor(s) 4. Visually check for refrigerant, oil or water leaks. 5. Open and close water valve. 6. Replace in-line water filter. 7. Check and clear ice machine draining system (drain vent and trap). 8. Clean motor, compressor and condenser coil 9. Check and tighten any loose screw-type electrical connection. 10. Inspect door(s) hinges, gaskets, handles; lubricate as required. 11. Clean area around equipment. 12. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-044S | 1. Remove ice from bin. 2. Cleaning: Mix a solution of 3 oz. manitowoc ice machine cleaner to 1 gallon of warm water. 3. Clean all internal surfaces and areas where lime scale has collected with the above solution. 4. Rinse all cleaned areas with fresh water. 5. Sanitizing: Mix a solution of 1 oz. manitowoc sanitizer with up to 4 gallons of water. 6. Wash all internal surfaces with this solution. 7. Rinse all internal surfaces with fresh water. 8. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-046Q | 1. Check fan operation and movement. 2. Spray moving parts when necessary 3. Clean fan blades,protective cover, motor etc. 4. Check wiring for frays and damage. | COMS_GEN MAINT
COMS-HVACR-050S | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks. 8. Tighten connections as required. 9. Replace air filters. 10. Clean coil(s). 11. Clean blower and motor as required. 12. Check electrical connections. 13. Clean area around unit. 14. Complete work order data. | COMS_CUP OPER
COMS-HVACR-100A | **Note: Annual PM must be performed in conjunction with Quarterly PM (HVAC-100Q). 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Clean evaporator drain pan, blower, motor, and drain piping. 3. Replace biocide unit. 4. Fill out maintenance checklist and report deficiencies via work request. | COMS_HVAC MECH
COMS-HVACR-100Q | 1. Check with operating or area personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Check operation and clean dampers, louvers and shutters; lubricate as required. 5. Check tension, condition, and alignment of belts, adjust as necessary. 6. Lubricate shaft and motor bearings. 7. Replace air filters. 8. Inspect exterior piping and valves for leaks; tighten connections as required. 9. Clean area around equipment. 10. Fill out maintenance checklist and report deficiencies via work request. | COMS_HVAC MECH
COMS-HVACR-112Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks. 8. Tighten connections as required. 9. Replace carbon air filters. 10. Clean area around unit. 11. Complete work order data | COMS_HVAC MECH
COMS-HVACR-113Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment, where applicable. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks, where applicable. 8. Check refrigerant pressure. Add or remove refrigerant, as required. 9. Tighten connections as required. 10. Replace carbon air filters. 11. Inspect, clean and adjust electrodes and nozzles on oil burners, where applicable. 12. Lubricate control valves and thermo-sensing bulbs on gas burners, where applicable. 13. Oil the burner motor bearings as applicable. 14. Inspect fuel system for leaks. 15. Inspect flame sensor for soot build-up and clean. 16. Change fuel filter element on oil burner, where applicable. 17. Check for proper operation of burner primary controls, check and adjust thermostat. 18. Check condition of flue pipe, damper and stack. 20. Check and clean condensate drain piping. 21. Clean area around unit. 22. Fill out maintenance checklist and report deficiencies. 23. Complete work order data | COMS_HVAC MECH
COMS-HVACR-114Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment. Adjust or replace belts as required. 6. Inspect exterior piping and valves for leaks. Inspect coils for debris. 7. Check refrigerant pressure. Add or remove refrigerant, as required. 8. Tighten connections as required. 9. Replace carbon air filters. 10. Clean area around unit. 11. Complete work order data | COMS_HVAC MECH
COMS-HVACR-200A | **Note: Annual PM must be performed in conjunction with Quarterly PM** 1. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 2. Check electrical wiring and connections; tighten loose connections. 3. Check refrigerant pressure; adjust refrigerant charge, if necessary. 4. Check compressor oil level; add oil as required. 5. Fill out maintenance checklist and report deficiencies via work request. 6. Complete work order data | COMS_HVAC MECH
COMS-HVACR-200Q | 1. Check with operating or area personnel for deficiencies. 2. Check controls and unit for proper operation, excessive noise or vibration. 3. Lubricate shaft bearings and motor bearings. 4. Inspect fan(s) or blower(s) for bent blades or imbalance; adjust as necessary. 5. Check belt(s) for condition, proper tension, and misalignment; adjust for proper tension and/or alignment, if necessary. 6. Inspect piping and valves for leaks; tighten connections as necessary. 7. Clean equipment and surrounding area 8. Fill out maintenance checklist and report deficiencies via work request. | COMS_HVAC MECH
COMS-HVACR-300A | **Note: Annual PM must be performed in conjunction with Quarterly PM (HVAC-300Q). 1. Clean coils, evaporator drain pan and condensate drain as required. 2. Clean blower and motor as required. 3. Check electrical connections. 4. Inspect VFD enclosure and clean, if applicable. 5. Check operation and clean dampers, louvers and shutters; lubricate as required. 6. Apply biocide. 7. Complete this in conjunction with the Quarterly PM 014Q. 8. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-300Q | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check for unusual noise or vibration. 4. Lubricate shaft and motor bearings. 5. Check belts for wear, tension and alignment, where applicable. 6. Adjust or replace belts as required. 7. Inspect exterior piping and valves for leaks, where applicable. 8. Check refrigerant pressure. Add or remove refrigerant, as required. 9. Tighten connections as required. 10. Replace air filters. 11. Inspect, clean and adjust electrodes and nozzles on oil burners, where applicable. 12. Lubricate control valves and thermo-sensing bulbs on gas burners, where applicable. 13. Oil the burner motor bearings as applicable. 14. Inspect fuel system for leaks. 15. Inspect flame sensor for soot build-up and clean. 16. Change fuel filter element on oil burner, where applicable. 17. Check for proper operation of burner primary controls, check and adjust thermostat. 18. Check condition of flue pipe, damper and stack. 20. Check and clean condensate drain piping. 21. Clean area around unit. 22. Fill out maintenance checklist and report deficiencies. 23. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-301Q | 1. Check with operating personnel for deficiencies. 2. Check tension, condition and alignment of belts, adjust as necessary. 3. Lubricate shaft and motor bearings. 4. Replace carbon air filters. 5. Perform operational check of unit, make adjustments on controls and other components as required. 6. During operation of unit, check refrigerant pressures, add refrigerant as necessary. 7. Inspect fuel system for leaks, repair any leaks found. 8. Check condition of flue pipe, damper and stack. 9. Clean area around unit. 10. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-350A | 1. Check filter, clean or change if needed 2. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 3. Drain water and cleaner from pan 4. Ensure proper drainage from condensate pan 5. Clean blower wheel and fan blades, lubricate if necessary 6. Clean vents and surrounding area 7. Complete work order data | COMS_HVAC MECH
COMS-HVACR-400A | 1. Check with operating personnel for deficiencies. 2. Check controls and unit for proper operation. 3. Check filter, clean or change if needed 4. Ensure proper drainage from condensate pan 5. Clean unit, including vents and surrounding area 6. Complete work order data | COMS_HVAC MECH
COMS-HVACR-700A | **NOTE: Annual PM must be performed in conjunction with Monthly, Quarterly, and Semiannual PM 1. Check all electrical connections, tighten as necessary. 2. Inspect all contacts and relays, replace as necessary. 3. Check accuracy of thermistors, replace if greater than +/- 2°F variance from calibrated thermometer. 4. Check to ensure that proper concentration of antifreeze is present in the chilled water loop. 5. Verify that the chilled water loop is properly treated. 6. Check refrigerant filter driers for excessive pressure drop, replace as necessary. 7. Check chilled water strainers, clean as necessary. 8. Replace bypass feeder filter bag. 9. Check cooler heater operation, if equipped. 10. Check condition of condenser fan blades and ensure they are securely fastened to the motor shaft. Lubricate shaft and motor bearings as required. 11. Perform Service Test to confirm operation of all components. 12. Check for excessive cooler approach (Leaving CHW Temp - Saturated Suction Temp) which may indicate fouling. 13. Clean cooler vessel if necessary. 14. Clean chiller and surrounding area. 15. Check outside of equipment for corrosion. | COMS_HVAC MECH
COMS-HVACR-700M | 1. Check moisture indicating sight glass for possible refrigerant loss and presence of moisture. 2. Clean intake side of condenser coils, fans, and intake screens. 3. Check chilled water supply and return temperatures, verify within normal operating range. 4. Complete work order data. | COMS_HVAC MECH
COMS-HVACR-700Q | **NOTE: Quarterly PM must be performed in conjunction with Monthly PM 1. Check refrigerant charge. 2. Check all refrigerant joints and valves for refrigerant leaks, repair as necessary. 3. Check chilled water flow switch operation. 4. Check all condenser fans for proper operation. 5. Check compressor oil level. 6. Check crankcase heater operation. | COMS_HVAC MECH
COMS-HVACR-700S | **NOTE: Semiannual PM must be performed in conjunction with Monthly and Quarterly PM 1. Check chilled water flow switch sensor tip for buildup, clean if necessary. 2. Remove any foreign objects or debris attached to the coil face or trapped within the mounting frame and brackets. 3. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. | COMS_HVAC MECH
COMS-HVACR-800A | 1. Isolate power and gas supplies 2. Unplug power connectors 3. Detach gas supply from unit 4. Detach ducted air supply 5. Remove burner from radiant tube 6. Remove gas injector and inspect for contamination or blockages, replace if necessary 7. Check pepper pot head for contamination, clean if necessary 8. Replace ignitor assembly 9. Remove combustion fan and clean with brush to remove any dust or contaminants 10. Inspect impeller for damage and ensure it rotates smoothly, replace if necessary 11. Remove any dust from the interior and exterior of burner tubes 12. Clean radiant heat reflectors 13. Clean fresh air inlet duct 14. Reassemble and place unit back in service | COMS_HVAC MECH
COMS-HVACR-900A | **NOTE: Maintenance shall be performed in conjunction with Quarterly PM ** 1. Lubricate evaporator blower. 2. Lubricate evaporator motor. 3. Clean coils with non-corrosive coil cleaner, vacuum cleaner, fresh water, compressed air under 50psi, or non-metallic bristle brush. Note: NO HIGH PRESSURE WATER. 4. Clean blower and drain pan as required. 5. Repack wheel bearings and replace retainers. 6. Examine springs and Ubolt connections. 7. Check brake lines for wear and any evidence of moisture or leaks on lines and fittings. 8. Check braking system for overall condition and operability. 9. Check wheel bolts and studs 10. Torque axle flange nuts | COMS_HVAC MECH
COMS-HVACR-900Q | 1. Check with operating personnel for deficiencies. 2. Perform operation checkout. 3. Check controls and unit for proper operation. 4. Check site glass moisture indicator for indication of moisture in coolant lines. 5. Check refrigerant pressure. Add or remove refrigerant as necessary. 6. Check filters and replace a necessary. 7. Check belts for wear. Tear, tension and adjustments. Adjust or replace as necessary. 8. Inspect flex tubing. 9. General condition of trailer. 10. Swivel jack operational and secure. 11. Tongue coupler and chains intact and in good working order. 12. Ensure lights in good working order. 13. Ensure proper torque of body mounting bolts. 14. Inspect tires for wear, and proper inflation. 15. Lubricate, latches, raisers, locks, handles. 16. Perform complete exterior inspection. 17. Check body for metal deterioration, squeaks, painting. 18. Check unit for overall cleanliness. 19. Complete work order data. | COMS_HVAC MECH
COMS-IE-001S | 1. Check with operating or area personnel for deficiencies. 2. Check for proper operation, binding or misalignment; adjust as necessary. 3. Check and lubricate door guides, pulleys and hinges. 4. Clean area around door. 5. Complete work order data. | COMS_GEN MAINT
COMS-IE-002S | 1. Check with operating or area personnel for deficiencies. 2. Check for proper operation, binding or misalignment; adjust as necessary. 3. Inspect and lubricate door guides, gearbox, and drive chain; adjust as necessary. 4. Clean area around door. 5. Complete work order data. | COMS_GEN MAINT
COMS-IE-003S | 1. Check with operating or area personnel for deficiencies. 2. Check for proper operation, binding or misalignment; adjust as necessary. 3. Check and lubricate door guides. 4. Inspect and lubricate motor gearbox, drive chain (or belt), and motor; adjust as necessary. 5. Check operation of limit switch; adjust as necessary. 6. Check electrical operator, wiring, connections and contacts; adjust as necessary. 7. Clean area around door. 8. Complete work order data. | COMS_GEN MAINT
COMS-IE-004A | 1. Check with door operating personnel for deficiencies. 2. Remove debris from door track. 3. Operate door. 4. Check alignment of hanger door, door guides and lubricate. 5. Inspect and lubricate wheel drive chain. 6. Adjust brake shoes and check for wear. 7. Complete work order data. | COMS_GEN MAINT
COMS-IE-004Q | 1. Check with door operating personnel for deficiencies. 2. Remove debris from door track. 3. Operate door. 4. Inspect and lubricate wheel drive chain. 5. Inspect and lubricate wheels, guides, stops and rollers. 6. Complete work order data. | COMS_GEN MAINT
COMS-IE-005A | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Inspect door gaskets for damage and proper fit; adjust gaskets as required and lubricate hinges. 4. Check door latch and adjust as necessary. 5. Clean area around equipment. 6. Complete work order data. | COMS_HVAC MECH
COMS-IE-006S | 1. Check for proper operation of pump. 2. Check for leaks on suction and discharge piping, seals, packing glands, etc.; make minor adjustments as required. 3. Check pump and motor operation for excessive vibration, noise and overheating. 4. Check alignment of pump and motor; adjust as necessary. 5. Lubricate pump and motor. 6. Inspect hydraulic lift post(s) for wear or leaks. 7. Inspect, clean and tighten valves. 8. Inspect and clean motor contactors. 9. Inspect and test control relays and check wiring terminals. 10. Clean pump unit and surrounding area. 11. Complete work order data. | COMS_GEN MAINT
COMS-IE-007A | 1. Check with operating or area personnel for deficiencies. 2. Inspect for damaged structural members, alignment, worn pins, column fasteners, stops and capacity markings. 3. Inspect and lubricate power cable tension reel; inspect condition of cable. 4. Check hoist operation - travel function, up, down, speed stepping, upper and lower travel limit switches, etc. 5. Inspect, clean and lubricate trolley assembly and reduction gear bushings. 6. Drain and replace reduction gear housing oil. 7. Inspect brake mechanism. 8. Inspect and clean hook assembly and chain or wire rope sheaves. 9. Inspect, clean and lubricate hoist motor. 10. Complete work order data. | COMS_GEN MAINT
COMS-IE-008A | 1. Check with operating or area personnel for deficiencies. 2. Inspect for damaged structural members, alignment, worn pins, column fasteners, stops and capacity markings. 3. Check hoist operation - travel function, up, down, etc. 4. Inspect, clean and lubricate pulley mechanism, etc. 5. Inspect and clean hook assembly and chain or wire rope sheaves. 6. Clean work area. 7. Complete work order data. | COMS_GEN MAINT
COMS-IE-010A | 1. Check with operating or area personnel for deficiencies. 2. Inspect crane for damaged structural members, alignment, worn pins, column fasteners, stops and capacity markings. 3. Inspect and lubricate power cable tension reel and inspect condition of cable. 4. Check operation of upper and lower travel limit switches. 5. Inspect brake mechanism. 6. Inspect, clean and lubricate trolley assembly and reduction gear bearings. 7. Drain and replace reduction gear housing oil. 8. Inspect and clean hook assembly and chain or wire rope sheaves. 9. Inspect, clean and lubricate hoist motor. 10. Check pendent control for hoist operation - travel function, up, down, speed stepping, etc. 11. Lubricate rails. 12. Inspect control cabinet. 13. Weight capacity test hoisting equipment at 150% of rated capacity. 14. Clean work area. 15. Complete work order data. | COMS_GEN MAINT
COMS-IE-010Q | 1. Check with operating or area personnel for deficiencies. 2. Inspect crane for damaged structural members, alignment, worn pins, column fasteners, stops and capacity markings. 3. Inspect and lubricate power cable tension reel and inspect condition of cable. 4. Check operation of upper and lower travel limit switches. 5. Inspect, clean and lubricate trolley assembly and reduction gear bearings. 6. Inspect and clean hook assembly and chain or wire rope sheaves. 7. Inspect, clean and lubricate hoist motor. 8. Check pendent control for hoist operation - travel function, up, down, speed stepping, etc. 9. Lubricate rails. 10. Inspect control cabinet. 11. Clean work area. 12. Complete work order data. | COMS_GEN MAINT
COMS-IE-011A | 1. Check for proper operation of pump. 2. Check for leaks on suction and discharge piping, seals, packing glands, etc.; make minor adjustments as required. 3. Check pump and motor operation for excessive vibration, noise and overheating. 4. Check alignment of pump and motor; adjust as necessary. 5. Lubricate pump and motor. 6. Inspect hydraulic lift post(s) for wear or leaks. 7. Inspect, clean and tighten valves. 8. Inspect and clean motor contactors. 9. Inspect and test control relays and check wiring terminals. 10. Clean pump unit and surrounding area. 11. Complete work order data. | COMS_GEN MAINT
COMS-IE-012S | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean fans and intake screens; lubricate motor. 4. Inspect door gaskets for damage and proper fit; adjust gaskets as required and lubricate hinges. 5. Check starter panels and controls for proper operation, burned or loose contacts, and loose connections. 6. Clean coils, evaporator drain pan, blowers, fans, motors and drain piping as required; lubricate motor(s). 7. During operation of unit, check refrigerant pressures and compressor oil level; add refrigerant and/or oil as necessary. 8. Check operation of low pressure cut-out; adjust or replace as required. 9. Inspect defrost systems for proper operation; adjust as required. 10. Clean area around equipment. 11. Complete work order data. | COMS_HVAC MECH
COMS-IE-013S | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean fans and intake screens; lubricate motor. 4. Inspect door gaskets for damage and proper fit; adjust gaskets as required and lubricate hinges. 5. Check starter panels and controls for proper operation, burned or loose contacts, and loose connections. 6. Clean coils, evaporator drain pan, blowers, fans, motors and drain piping as required; lubricate motor(s). 7. During operation of unit, check refrigerant pressures and compressor oil level; add refrigerant and/or oil as necessary. 8. Check operation of low pressure cut-out; adjust or replace as required. 9. Inspect defrost systems for proper operation; adjust as required. 10. Clean area around equipment. 11. Complete work order data. | COMS_HVAC MECH
COMS-IE-015Q | 1. Check with operating or area personnel for deficiencies. 2. Check electric motor, controls, wiring connections, insulation and contacts for damage and/or proper operation; adjust as required. 3. Check V-belt for wear, tension and alignment; change/adjust belt as necessary. 4. Lubricate bushings and check oil level in gear drive mechanism; add oil if required. 5. Clean machine of dust, grease and food particles. 6. Check motor and motor bearings for overheating. 7. Check for loose, missing or damaged nuts, bolts, or screws; tighten or replace as necessary. 8. Complete work order data. | COMS_ELEC
COMS-IE-016Q | 1. Check with operating or area personnel for any deficiencies. 2. Check operation of mixer at varying speeds for excessive noise and vibrations; align or adjust as required. 3. Tighten loose bolts, nuts, and screws. 4. Check oil level in transmission; add or replace oil if required. 5. Lubricate mixer gears and bowl lift mechanism. 6. Check switches and control for damage and proper operation; adjust as required. 7. Check belt for proper tension and alignment; adjust as required. 8. Clean machine of dust and grease. 9. Check anchor bolts for tightness; tighten as required. 10. Clean area around equipment. 11. Complete work order data | COMS_ELEC
COMS-IE-018M | 1. Check with operating or area personnel for any deficiencies. 2. Check doors and seals for warping and misalignment; lubricate hinges and repair as necessary. 3. Check nuts, bolts, and screws for tightness; replace or tighten as required. 4. Check element, switches, controls and wiring on electrically heated units for defects; repair as required. 5. Check operation of thermostat; calibrate as required. 6. Complete work order data. | COMS_ELEC
COMS-IE-019M | 1. Check with operating or area personnel for any deficiencies. 2. Check compartments, valves, and piping for leaks; tighten as required. 3. Check thermostat; calibrate if necessary. 4. On electrically heated units check elements, switches, controls, contacts, and wiring for defects; repair or adjust as necessary. 5. Check basket or rack for bends, breaks or defects, straighten bends or repair as necessary. 6. Check nuts, bolts and screws for tightness; tighten or replace as necessary. 7. Complete work order data. Provide Equipment information | COMS_ELEC
COMS-IE-020M | 1. Check with operating or area personnel for any deficiencies. 2. Check doors and seals for warping and misalignment; lubricate hinges and repair as necessary. 3. Check nuts, bolts, and screws for tightness; replace or tighten as required. 4. Check element, switches, controls and wiring on electrically heated units for defects; repair as required. 5. Check operation of thermostat; calibrate as required. 6. Complete work order data. | COMS_ELEC
COMS-IE-022M | 1. Check with operating or area personnel for any deficiencies. 2. Check doors and seals for warping and misalignment; lubricate hinges and repair as necessary. 3. Check nuts, bolts, and screws for tightness; replace or tighten as required. 4. Check element, switches, controls and wiring on electrically heated units for defects; repair as required. 5. Check fan blades and fan motor for proper operation. 6. Check operation of thermostat; calibrate as required. 7. Complete work order data. | COMS_ELEC
COMS-IE-023Q | 1. Check with operating or area personnel for any deficiencies. 2. Check piping and fittings for leaks; tighten as required. 3. Check operation of electric water valve. 4. Inspect cover, hinges, and seals on units to equipped; lubricate hinge. 5. Lubricate tilting gear mechanism and trunnion bearings, if applicable. 6. Complete work order data. | COMS_ELEC
COMS-IE-024Q | 1. Check with operating or area personnel for deficiencies. 2. Check electric transformer, heating elements, insulators, connections and wiring; tighten connections and repair as required. 3. Check surface temperature with meter for hot spots. 4. Check piping and valves on gas operated units for leaks. 5. Check pilot/igniter, burner and combustion chamber for proper operation; adjust as required. 6. Check temperature control system for proper operation; adjust as required. 7. Lubricate tilting gear mechanism and trunnion bearings. 8. Check nuts, bolts and screws for tightness; tighten as required. 9. Check complete operation of unit. 10. Complete work order data. | COMS_ELEC
COMS-IE-025Q | 1. Check with operating or area personnel for any deficiencies. 2. Examine doors and door gaskets; make necessary adjustments. 3. Visually inspect hinges and latches; lubricate hinges. 4. Tighten or replace any loose nuts, bolts, screws; replace broken knobs. 5. Check for clogged or defective steam trap; clean trap. 6. Inspect and clean steam strainer. 7. Check working pressure on steam gauge. 8. Turn unit on, allow pressure to build, inspect piping, valve and doors for leaks; adjust as required. 9. Check operation of pressure relief valve; adjust as required. 10. Check operation of low water cut-off; adjust as required. 11. Check water level sight glass; adjust as required. 12. Check timer mechanism and operation; adjust as required. 13. Complete work order data. | COMS_ELEC
COMS-IE-026Q | 1. Check with operating or area personnel for any deficiencies. 2. Check piping and fittings for leaks; tighten as required. 3. Check operation of electric water valve. 4. Inspect cover, hinges, and seals on units to equipped; lubricate hinge. 5. Lubricate tilting gear mechanism and trunnion bearings, if applicable. 6. Complete work order data. | COMS_ELEC
COMS-IE-027Q | 1. Check thermostat, switch, and temperature gauge; calibrate if required. 2. Check pilots and flame on gas operated units; adjust as required. 3. Check working pressure on steam operated unit. 4. Check electrical connections and wiring for defects; tighten connections. 5. Check for clogged or defective steam trap. 6. Inspect and clean steam strainer. 7. Examine equipment, valves, and piping for leaks. 8. Inspect for leaks at water gauge glasses and at valves; repack valves if necessary. 9. Tighten or replace loose, missing, or damaged nuts, bolts, or screws. 10. Lubricate water filter valve, check rings, tighten as required. 11. Check operation of lights. 12. Check timer mechanism and operation of unit. 13. Complete work order data. | COMS_ELEC
COMS-IE-029A | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean area around equipment. 4. Complete work order display. | COMS_HVAC MECH
COMS-IE-031A | 1. Check with operating or area personnel for deficiencies. 2. Clean heating elements, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean area around equipment. 4. Complete work order display. | COMS_ELEC
COMS-IE-032Q | 1. Check with operating or area personnel for any deficiencies. 2. Check nuts, bolts and screws for tightness; tighten or replace as required. 3. On gas operated units, check piping and valves for leaks. 4. On gas operated units, check pilot and gas burners for uniform flame; adjust as required. 5. On electrically operated units, check switches, connections, and wiring for proper operation; adjust as required. 6. Check calibration of thermostats; adjust as required. 7. Complete work order data. | COMS_ELEC
COMS-IE-034M | 1. Check with operating or area personnel for any deficiencies. 2. Clean machine thoroughly of dust, grease, and food particles.(kitchen contractor responsibility) 3. Check compartments, valves, and piping for leaks; tighten as required. 4. Check thermostat; calibrate if necessary. 5. On electrically heated units check elements, switches, controls, contacts, and wiring for defects; repair or adjust as necessary. 6. Check basket or rack for bends, breaks or defects, straighten bends or repair as necessary. 7. Check nuts, bolts and screws for tightness; tighten or replace as necessary. 8. Complete work order data. | COMS_ELEC
COMS-IE-035A | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean area around equipment. 4. Complete work order display. | COMS_HVAC MECH
COMS-IE-036A | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean area around equipment. 4. Complete work order display. | COMS_HVAC MECH
COMS-IE-040A | 1. Check with operating or area personnel for deficiencies. 2. Clean heating elements, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean area around equipment. 4. Complete work order display. | COMS_ELEC
COMS-IE-041A | 1. Check with operating or area personnel for deficiencies. 2. Clean coils, fans, fan motors, drip pan and other areas with vacuum, brush or wiping as necessary. 3. Clean area around equipment. 4. Complete work order display. | COMS_HVAC MECH
COMS-IE-042Q | 1. Check with operating or area personnel for deficiencies. 2. Remove access panels and clean coils, fans, fins, and other areas (vacuum, blow down with compressed air or CO2, and/or wipe off). 3. Lubricate motor bearings. 4. Check electrical wiring and connections; tighten loose connections. 5. Visually check for refrigerant, water, and other liquid leaks. 6. Check door gaskets for proper sealing; adjust door catch as required. 7. Inspect dispensing valves; adjust as necessary. 8. Perform operational check of unit; make adjustments as necessary. 9. Clean area around equipment. 10. Complete work order data. | COMS_HVAC MECH
COMS-IE-043Q | 1. Check with operating or area personnel for deficiencies. 2. Inspect lid gasket for damage and proper fit; adjust and/or repair as necessary. 3. Clean out inside of grease interceptor. 4. Tighten bolts on lid. 5. Clean area around equipment. 6. Complete work order display. | COMS_PLUMBER
COMS-IE-044Q | 1. Check with operating or area personnel for any deficiencies. 2. Check electric insulators, connections, and wiring (includes removing access panels). 3. Check motor and bearings for excessive noise, vibration and overheating. 4. Check dish conveyor by turning on switch and observing conveyor movement; adjust chain if necessary. 5. Check operation of wash and rinse spray mechanism for spray coverage and drainage. 6. Inspect soap and spray solution feeder lines, steam and water lines and fittings for leaks; clean and tighten fittings as necessary. 7. Lubricate conveyor drive bushings and chain drive, check belt tension and adjust if required. 8. Check doors for: operation of chains and counterweights, warping, alignment and water tightness; adjust if necessary. 9. Tighten loose nuts, bolts and screws. 10. Check packing glands on wash, rinse, and drain valves; add or replace packing as required. 11. Check lubricant in gear case; add oil if required. 12. Inspect splash curtain for tears, clearance and water tightness; adjust if required. 13. Check proper operation of solenoid valve and float in fill tank; adjust as required. 14. Check pumps for leakage and obstructions; adjust as required. 15. Check proper operation of micro-switch and water for proper temperature readings. 16. Check operation of safety stop and clutch on conveyor belt motor; adjust cut-off switch mechanism as required. 17. Check temperature regulator and adjust if necessary. 18. Clean lime off thermostatic probe and area around equipment. 19. Perform plate test with temperature sensoring tape, use 160 degree f / 71 degree c. Record results and record on PM work order and give plate test to the Kitchen Manager. 20. Complete work order data. | COMS_PLUMBER
COMS-IE-045Q | 1. Check with operating or area personnel for deficiencies. 2. Check cutting surfaces, clutch assembly and guards for damage and proper alignment; adjust as required. 3. Check nuts, bolts, and screws for tightness; tighten or replace as required. 4. Check switch and controls for proper operation; adjust as required. 5. Check operation of motor and check motor bearings for overheating; lubricate as required. 6. Check belt tension; replace belt and/or adjust if required. 7. Complete work order data. | COMS_ELEC
COMS-IE-046Q | 1. Check with operating or area personnel for any deficiencies. 2. Check motor and drive shaft for excessive noise, vibration, overheating, etc. 3. Inspect electrical wiring and connections. 4. Check drive belt(s) for wear and tension; adjust if required. 5. Check electrical switch for proper operation. 6. Check and tighten all nuts, bolts and screws as necessary. 7. Complete work order data. | COMS_GEN MAINT
COMS-IE-047S | 1. Check alignment of rollers and gate. 2. Grease rollers. 3. Oil latch. 4. Complete work order data. | COMS_GEN MAINT
COMS-IE-049S | 1. Check with operating or area personnel for deficiencies. 2. Check motor and motor bearings for excessive noise, vibration, overheating, etc. 3. Inspect electrical wiring and connections. 4. Check drive belt(s) and/or shaft for wear and tension; adjust if required. 5. Check electrical switches and controls for proper operation. 6. Check for loose, missing or damaged nuts, bolts, or screws; tighten or replace as necessary. 7. Clean area around equipment. 8. Complete work order data. | COMS_GEN MAINT
COMS-IE-059M | 1. Inspect drive for excessive slack; adjust as necessary. 2. Inspect limit switch and brake; adjust as necessary. 3. Inspect sprockets for wear and tightness; adjust as necessary. Electronic Technician 1. Check safety loop- verify gate reverses or stops. 2. Check edge guards, transmitters and receiver - verify gate reverses or stops. 3. Check infrared photo cell transmitters and receivers - verify gate reverses or stops, 4. Replace batteries in tranmitters every 3 years. | COMS_GEN MAINT
COMS-IE-059S | 1.Check alignment of rollers and gate and adjust as necessary. 2. Grease rollers. 3. Oil latch. 4. Check electric motor and connections. Make repairs as required. | COMS_GEN MAINT
COMS-IE-061Q | 1. Check with building personnel for report of water softener effectiveness. 2. Check pressure gauges for proper operation. 3. Check density of brine solution in salt tank. 4. Check operation of float control in brine. 5. Inspect water softener piping, fittings and valves for leaks. 6. Lubricate valves and motors. 7. Make minor adjustments to water softener controls if required. 8. Inspect softener base and brine tank for corrosion and repair as needed. 9. Check operation of automatic fill valve in brine tank. 10. Check softener electrical wiring and phasing. 11. Clean up around softener. 12. Complete work order data. | COMS_PLUMBER
COMS-IE-062A | 1.Check unit and verify proper operation of mechanical functions. 2.Change filter. 3.Clean sludge from bottom of unit. 4.Check fluid light and fill to proper level of fluids. 5.Complete work order data. | COMS_GEN MAINT
COMS-IE-062M | 1.Check unit and verify proper operation of mechanical functions. 2.Change filter. 4.Check fluid light and fill to proper level of fluids. 5.Complete work order data. | COMS_GEN MAINT
COMS-IE-063S | 1. Check operation of the lift 2. Check oil level 3. Check for leaks 4. Check roller bushings, axle pin, clevis and pivot points for wear 5. Check oil heater operation (if so equiped) 6. Check for unusual noise 7. Check hose and electrical wiring and connections | COMS_GEN MAINT
COMS-IE-064S | 1.Inspect interior of building for signs of leaks. 2.Inspect building exterior for settlement, movement and moisture. 3.Inspect for any debris on the roof and remove. 4.Inspect for and remove any containments (grease, chemicals, liquids, etc) on the roof. 5.Inspect for any loose, missing deformed or damaged gutters. 6.Inspect for any loose, missing, deformed or damaged downspouts. 7.Inspect for any damage or missing parts of roof and overflow drains. 8.Inspect for any damage to scuppers. 9.Inspect for roof drains, overflow drains and scuppers to be securely attached. 10.Clean gutters, downspouts, roof drains, overflow drains and scuppers. 11.Inspect gutters, downspouts, roof drains, overflow drains and scuppers for unimpeded water flow and discharge. 12.Inspect for visible deflection in roof slope. 13.Inspect for positive drainage. 14.Inspect for signs of standing water (accumulated dried, debris, discoloration). 15.Inspect for excessive standing water (an area of 100 SF or more which holds in excess of 1/2" of water at deepest point after a rain fall). 16.Inspect for loose, missing or deformed weather seals of equipment in area of roof. 17.Inspect for leaks, discharges or drainage from equipment in the area of the roof. 18.Inspect for vibration or motion damage by equipment in the area of the roof. 19 Inspect construction adjoining roof (parapets, walls, etc.) for damage (cracking, spalling, discoloration etc.). 20.Inspect for damage due to differential movement of construction adjoining roof. 21.Inspect for clear weep holes in adjoining construction. 22.Inspect for loose, missing, deformed or damaged flashing at equipment curbs and supports. 23.Inspect for loose, missing, deformed or damaged flashing at roof penetrations. 24.Inspect for loose, missing, deformed or damaged flashing at roofing material terminations (counter flashing, expansion joint covers). 25.Inspect for loose, missing, deformed or damaged coping. 26.Inspect for loose, missing, deformed or damaged edge metal. 27.Inspect for loose, missing, deformed or damaged clamping rings. 28.Inspect for flashing pulled away from angled intersections. 29.Inspect for cracked, sunken, missing or aged sealants. 30.Inspect for rusted or corroded metal. 31.Inspect for loose, missing, deformed or damaged pitch pockets 32.Inspect for pitch pocket sealant to be filled, thoroughly adhered and not aged. 33.Inspect for loose, missing, deformed or damaged reglets. 34.Inspect for loose, missing, deformed or damaged termination bars. 35.Inspect for all roof curbs, equipment supports and roof penetrations to be securely attached to roof structure. 36.Inspect for weather seal at top of all penetration flashings. 37.Inspect for all fasteners to be secure. 38.Inspect for equipment, pads, ladders resting on or settling into roof surface where not designed to rust on roof. 39.Inspect for water cascading onto roof from another roof or source. 40.Inspect for cuts, slices, splits and punctures of the membrane. 41.Inspect for swelling, buckling, wrinkling, cracking and bubbling of the membrane. 42.Inspect for worn or deteriorated areas of the membrane. 43.Inspect for open, bubbled, ridged, fish-mouthed and unadhered areas of horizontal and vertical membrane lap seams. 44.Inspect for cracked, flaking, blistered and discontinuous areas of any protective surface coating. 45.Inspect for changes in insulation or substrate firmness as the roof is walked upon. 46.Inspect for displaced, deflected and distorted insulation or substrate. 47.Inspect for tenting and loose insulation or substrate fasteners. 48.Inspect ballasted membrane for missing and displaced ballast. 49.Inspect adhered and mechanically attached membrane for unadhered and unattached membrane. 50.Inspect membrane for disbanding and delamination. 51.Complete work order data. | COMS_GEN MAINT
COMS-IE-065A | 1. Check latch bolt holes for debris & clean as necessary. 2. Vacuum for water or other debris from the 114 door floor latch bolt holes. 3. Ensure all tensioners are keeping chain taut (hand tight is sufficient for this application). 4. Apply grease to all fittings, five locations on 118A & 119A, three locations on 114. 5. Apply Boeshield to all latch bolts and latch bolt pins. 6. Apply CRC aerosol dry lubricant to all chains. 7. Complete work order data. | COMS_GEN MAINT
COMS-IE-066S | 1. Grease Hinges. 2. Check door operation opens and closes and latches properly. 3. Check for rusting and chipping on paint. 4. Lubricate pivot points on latch, lever and exit device. 5. Lubricate cylinder and check key operation. 6. Complete all paperwork. | COMS_GEN MAINT
COMS-IE-900Q | 1. Check compressor oil, add oil if required. 2. Perform operation check of compressor system. 3. Check motor operation for excessive vibration and noise. 4. Lubricate motor. 5. Check operation of pressure relief valve. 6. Clean cooling fans and air cooler on compressor. 7. Check tension, condition, and alignment of V-belts; adjust as necessary. 8. Drain moisture from air storage tank, check for corrosion. 9. Clean air intake filter on compressor. 10. Clean oil and water trap. 11. Clean compressor and surrounding area. 12. Complete work order data. | COMS_GEN MAINT
COMS-IE-900S | **Note: Semiannual PM must be performed in conjunction with Quarterly PM (IE-900Q) 1. Replace compressor oil. 2. Complete work order data. | COMS_GEN MAINT
COMS-IE-930A | **Note: Semiannual PM must be performed in conjunction with Semiannual and Quarterly PM (IE-930S & IE-930Q). 1. Change the compressor oil and oil filter. Oil: ROTOROIL 8000 F2. 2. Note any large oil consumption or high pressure drop across the air-oil separator. 3. Replace the air-oil separators. Cover screws: 145 ft-lb. 4. Replace the oil return valves and associated o-ring. (Skip Step 8 of IE-930Q during annual PM) 5. Remove and replace the servo valve filter. 5. Complete work order information. | COMS_EQUIP MECH
COMS-IE-930Q | 1. Check with area personnel for any deficiences. 2. Check compressor oil level. Oil should be exceed the oil level indicator when unit is not operating and without pressure. When running, oil level should reach half the level indicator. Wait 15 minutes after shutdown to allow for settling. 3. Check and clean out Y-strainer on compressor and tank. 4. Check and clean solenoid valve filter of condensate drain. 5. Remove and clean suction filter with compressed air from inside to outside. 6. Remove fan guard panel and clean oil/air radiator with compressed air from top to bottom. 7. Remove and clean pre-filter of suction grids. Do NOT use any solvents. 8. Remove and clean the oil return valve. Clean with detergent and blow off with compressed air. Be sure to check integrity of o-rings. Do NOT overtighten banjo bolts. Note excessive scaling on sintered filter. 9. Check all rubber hoses for leaks and cracking. 10. Confirm all unit setpoints and run settings are correct. 11. Record total, run, and load hours. 12. Clean unit and surrounding area. 13. Complete work order information. | COMS_EQUIP MECH
COMS-IE-930S | **Note: Semiannual PM must be performed in conjunction with Quarterly PM (IE-930Q). 1. Replace the suction filters. 2. Tighten wire connections in command & control electrical board and terminal board of the motor. 3. Lubricate the motor bearings. 4. Complete work order information. | COMS_EQUIP MECH
COMS-IE-935A | **Note: Annual PM must be performed in conjunction with Semiannual and Quarterly PM (IE-935S & IE-935Q). 1. Change the compressor oil and oil filter. Oil: ROTOROIL 8000 F2. 2. Note any large oil consumption or high pressure drop across the air-oil seperator. 3. Replace the air-oil separators. Replace all sealing rings (O-Rings) during process. 4. Replace the oil return valves and associated O-rings. (Skip Step 9 of IE-935Q during annual PM) 5. Complete work order information. | COMS_EQUIP MECH
COMS-IE-935Q | 1. Check with area personnel for any deficiences. 2. Check compressor oil level. Oil should be exceed the oil level indicator when unit is not operating and without pressure. When running, oil level should reach half the level indicator. Wait 15 minutes after shutdown to allow for settling. 3. Check and clean out Y-strainer on compressor and tank. 4. Check and clean condensate drain solenoid valve filter. 5. Remove and clean the pre-filter suction grids. Do NOT use any solvents. 6. Clean the oil cooler from top to bottom, opposite of air flow. 7. Clean the compressed air after cooler from top to bottom, opposite of air flow. 8. Clean the air intake filter, housing, and cover with compressed air. 9. Remove and clean oil return valves. Clean with detergent and blow off with compressed air. ALWAYS replace the five (5) O-rings before reinstalling the O.R.V. Do NOT overtighten the banjo bolts on the O.R.V. assembly. Note excessive scaling on sintered filter. 10. Check all rubber hoses for leaks and cracking. 11. Confirm all unit setpoints and run settings are correct. 12. Record total, run, and load hours. 13. Clean unit and surrounding area. 14. Complete work order information. | COMS_EQUIP MECH
COMS-IE-935S | **Note: Semiannual PM must be performed in conjunction with Quarterly PM (IE-935Q). 1. Replace the air intake filter. 2. Tighten wire connections inside the start and control panel and inside the motor terminal board. 3. Lubricate the motor bearings. 4. Complete work order information. | COMS_EQUIP MECH
COMS-IE-940Q | 1. Perform operation check of compressor system. 2. Clean cooling fans and acompressor 3. Check tension, condition, and alignment of belts; adjust as necessary. 4. Drain moisture from air storage tank, check for corrosion. 5. Clean air intake filter on compressor. 6. Clean oil and water trap. 7. Clean compressor and surrounding area. 8. Check compressor electrical system. 9. Check coolant level add if necessary. 10. Complete work order data. | COMS_GEN MAINT
COMS-IE-940S | 1. Perform operation check of compressor system. 2. Clean cooling fans and air cooler on compressor. 3. Check tension, condition, and alignment of belts; adjust as necessary. 4. Drain moisture from air storage tank, check for corrosion. 5. Clean air intake filter on compressor. 6. Clean oil and water trap. 7. Clean compressor and surrounding area. 8. Check air compressor motor lubrication and grease if necessary. 9. Check electrical and safety shutdown devices. 10. Change oil filter element. 11. Replace if needed coolant. 12. Change separator element. 13. Compete work order data. 14. Dispose of all waste items thru enviornmental. | COMS_GEN MAINT
COMS-IE-945Q | 1. Perform operation check of compressor system. 2. Disconnect electrical power supply to unit. 2. Vent all air lines. 3. Remove Filter Cover. 4. Check Filter Felt. Replace Felt if it is covered with contamination or shows signs of increasing differential pressure. 5. Reinstall Felt and Filter Cover. 6. Clean compressor body in its entirety. 7. Compete work order data. | COMS_EQUIP MECH
COMS-IE-945A | **Annual PM Must Be Performed in conjunction with Quarterly PM (IE-945Q) 1. Disassemble Compressor Head. 2. Check Thickness of Rider Ring. 3. If Rider Ring is less than 0.055" Thick, Replace, Otherwise, record thickness and reuse. 4. Reassemble Compressor head. | COMS_EQUIP MECH
COMS-PC-001M | 1. Comply with monthly inspections of facility. 2. Spray with appropriate chemical and/or set traps for removal and prevention. 3. Complete work order data. | COMS_PEST CTRL
COMS-PC-001W | 1. Comply with weekly inspections of showers. 2. Apply appropriate insecticide. 3. Complete work order data. | COMS_PEST CTRL
COMS-PC-002W | 1. Comply with weekly inspections of cafeterias/breakrooms. 2. Apply appropriate insecticide. 3. Complete work order data. | COMS_PEST CTRL
COMS-PC-003S | 1. Apply herbicide and hand trim along fenceline 2. Ensure gate is free and clear for proper operation. 3. Complete work order data. | COMS_PEST CTRL
COMS-PC-004M | 1. Comply with Monthly Reports as follows:. NJ DEP Usage Report Pesticide Inventory Turf/Ornamental Report Stored Products-Pest Report 2. Complete work order data. | COMS_PEST CTRL
COMS-PL-001S | 1. Check with operating or area personnel for deficiencies. 2. Check for water leaks to tank and piping. Check for fuel system leaks. 3. Check gas burner and pilot for proper flame; adjust if required. 4. Check operation and condition of pressure relief valve. 5. Check automatic controls for proper operation (temperature regulators, thermostatic devices, automatic fuel shut off valve, etc.). 6. Check draft diverter and clear openings, if clogged. 7. Check electrical wiring for fraying and loose connections on gas burner. 8. Check for proper water temperature setting; adjust as required. 9. Check condition of flue pipe, and chimney. 10. Drain sediment from tank. 11. Clean up area around unit. 12. Inspect all hot water system piping insulation. Repair or replace as necessary. 13. Complete work order data. | COMS_PLUMBER
COMS-PL-002S | 1. Check with operating or area personnel for deficiencies. 2. Check for water leaks to tank and piping. 3. Check operation and condition of pressure relief valve. 4. Check electrical wiring connections on controls and switches. 5. Check for proper water temperature setting; adjust as required. 6. Clean, test and inspect sight gauges, valves and drains. 7. Check automatic controls for proper operation (temperature regulators and thermostatic devices). 8. Check insulation on heater; repair as necessary. 9. Drain sediment from tank. 10. Clean up area around unit. 11. Inspect all hot water piping insulation. Repair or replace as necessary. 12. Complete work order data. | COMS_PLUMBER
COMS-PL-003S | 1. Check with operating or area personnel for deficiencies. 2. Check for water leaks to piping. 3. Check electrical wiring connections on controls and switches. 4. Check for proper water temperature setting; adjust as required. 5. Clean, test and inspect valves and drains. 6. Check automatic controls for proper operation (temperature regulators and thermostatic devices). 7. Clean up area around unit. 8. Inspect all hot water piping insulation. Repair or replace as necessary. 9. Complete work order data. | COMS_PLUMBER
COMS-PL-004A | **Note: Annual PM must be performed in conjunction with Semi Annual PM** 1. Perform a annual pump out to remove grease, grit and other debris. 2. Pressure Wash Walls With Cleaning Agent 3. Pump Out Water And Cleaning Agent 4. Lubricate check valves and rails 5. Complete work order data | COMS_PLUMBER
COMS-PL-004S | 1. Check for proper operation of pump. 2. Check for leaks on suction and discharge piping, seals, packing glands, etc.; make minor adjustments as required. 3. Check ejector and motor operation for excessive vibration, noise and overheating. 4. Check float or pressure controls for proper operation. 5. Inspect the lights and alarm system. 6. Complete work order data | COMS_PLUMBER
COMS-PL-006S | 1. Check with operating personnel for any deficiencies. 2. Remove pump from pit. 3. Clean out trash from pump intake. 4. Check electrical plug, cord and connection. 5. Inspect pump body for corrosion; prime and paint as necessary. 6. Check pump and motor operation for excessive vibration, noise and overheating. 7. Lubricate pump and motor, where applicable. 8. Return pump to pit; reset and check float switch for proper operation. 9. Clean area. 10. Complete work order data. | COMS_PLUMBER
COMS-PL-007S | 1. Check with operating personnel for any deficiencies. 2. Check packing for leaks; tighten or repack as necessary. 3. Lubricate electric motor as required. 4. Inspect operation of discharge valve. 5. Inspect electrical system for frayed wires or loose connections; repair as necessary. 6. Check operation of pressure and thermal controls. 7. Run pump and check for noise and vibration. 8. Complete work order data. | COMS_PLUMBER
COMS-PL-009S | 1. Check with pump operating personnel for any known deficiencies. 2. Check for leaks on suction and discharge piping, seals, etc. 3. Check pump and motor operation for vibration, noise, overheating, etc. 4. Check alignment and clearances of shaft and coupler. 5. Tighten or replace loose, missing, or damaged nuts, bolts, and screws. 6. Lubricate pump and motor as required. 7. Clean pump, motor and surrounding area. 8. Complete work order data. | COMS_PLUMBER
COMS-PL-010S | 1. Check with operating or area personnel for deficiencies. 2. Check for leaks on discharge piping and seals, etc. 3. Check pump and motor operation for vibration, noise, overheating, etc. 4. Check alignment and clearances of shaft and coupler. 5. Tighten or replace loose, missing, or damaged nuts, bolts, and screws. 6. Lubricate pump and motor as required. 7. Clean pump, motor and surrounding area. 8. Complete work order data. | COMS_PLUMBER
COMS-PL-011Q | 1. Check for proper operation of pump. 2. Check for leaks on suction and discharge piping, seals, packing glands, etc.; make minor adjustments as required. 3. Check pump and motor operation for excessive vibration, noise and overheating. 4. Check alignment of pump and motor, adjust as necessary. 5. Lubricate pump and motor. 6. Clean exterior of pump, motor and surrounding area. 7. Complete work order data. | COMS_PLUMBER
COMS-PL-011S | 1. Check for proper operation of pump. 2. Check for leaks on suction and discharge piping, seals, packing glands, etc.; make minor adjustments as required. 3. Check pump and motor operation for excessive vibration, noise and overheating. 4. Check alignment of pump and motor, adjust as necessary. 5. Lubricate pump and motor. 6. Clean exterior of pump, motor and surrounding area. 7. Complete work order data. | COMS_PLUMBER
COMS-PL-013S | 1. Check with operating or area personnel for deficiencies. 2. Check for leaks on suction and discharge piping, seals, etc. 3. Check pump and motor operation for excessive vibration, noise and overheating. 4. Check alignment and clearances of shaft and coupler. 5. Tighten or replace loose, missing, or damaged nuts, bolts and screws. 6. Lubricate pump and motor as required. 7. Clean pump, motor and surrounding area. 8. Complete work report data. | COMS_PLUMBER
COMS-PL-014A | 1. Test and calibrate check valve operation of backflow prevention device with test set. 2. Bleed air from backflow preventer. 3. Inspect for leaks under pressure. 4. Clean backflow preventer and surrounding area. 5. Complete work report data. | COMS_PLUMBER
COMS-PL-017Q | 1. Check with operating or area personnel for any deficiencies. 2. Check motor and drive shaft for excessive noise, vibration, overheating, etc. 3. Inspect electrical wiring. 4. Visually examine grinder, check for obstructions; adjust cutters if required. 5. Check drive belt(s) for wear and tension; adjust if required. 6. Check for leaks to supply and drain connections; tighten if required. 7. Check electrical switch for proper operation 8. Lubricate grinder, drive and motor. 9. Check water sprayer operation. 10. Complete work report data. | COMS_PLUMBER
COMS-PL-018A | 1. Inspect exterior of tank for leaks or damage. 2. Inspect valves, fittings, drains and controls for leakage or damage. 3. Check for deterioration of tank foundation and supports. 4. Clean up around tank. 5. Complete work report data. | COMS_PLUMBER
COMS-PL-020Q | 1. Check compressor oil level; add oil as necessary. 2. Perform operational check of compressor system and adjust as required. 3. Check motor for excessive vibration, noise and overheating; lubricate. 4. Check operation of pressure relief valve. 5. Clean cooling fans and air cooler. 6. Check tension, condition, and alignment of V-belts; adjust as necessary. 7. Drain moisture from air storage tank and check low pressure cut-in; while draining, check discharge for indication of interior corrosion. 8. Replace air intake filter, as needed. 9. Clean oil and water trap. 10. Clean compressor and surrounding area. 11. Complete work report data. | COMS_GEN MAINT
COMS-PL-023Q | 1. Check with operating personnel for deficiencies. 2. Clean compressor air filter. 3. Check drive belts for condition and tension. 4. Change compressor oil. 5. Clean air dryer and surrounding area. 6. Complete work report data. | COMS_HVAC MECH
COMS-PL-025A | 1. Check unit for proper operations, excessive noise or vibration. 2. Clean condenser coils and fan as required. 3. Check for water leaks in supply line and drain. 4. Check water flow, adjust as necessary. 5. Check drinking water temperature to ensure the unit is operating properly. 6. Check electrical connections and cord; tighten and repair as necessary. 7. Clean area around fountain. 8. Complete work report data. | COMS_PLUMBER
COMS-PL-028Q | 1. Check for damaged or missing parts. 2. Remove filter. 3. Install new filter. 4. Complete work order data. | COMS_PLUMBER
COMS-PL-030M | 1. Remove strainer. 2. Remove debris from strainer. 3. Remove any visable clogs from drain pipe. 4. Replace strainer. 5. Add water to drains that normally have no flow to fill traps to prevent odors from entering building. 6. Complete work order data. | COMS_PLUMBER
COMS-PL-030Q | 1. Locate drain by grid provided. 2. Remove carpet tile to access strainer, then clean debris from top of strainer. 3. Remove any visible clogs from drain pipe above strainer. 4. Fill drain with water to provide proper water seal. 5. Replace carpet tile. 6. Complete work order data. | COMS_PLUMBER
COMS-PL-031A | 1. Check expiration date on bottles. 2. Check for leaks or breaks on bottles. 3. Clean unit. 4. Ensure unit is free from obstruction and ready for use. | COMS_PLUMBER
COMS-PL-031Q | 1. Turn water on and off to verify proper operation. 2. Remove spray head. 3. Check spray head. 4. Install spray head. 5. Complete work order data. | COMS_PLUMBER
COMS-PL-031W | 1. Turn water on and off to verify proper operation. 2. Complete work order data. | COMS_PLUMBER
COMS-PL-032Q | 1. Turn water on and off to verify proper operation. 2. Remove spray head. 3. Check shower head. 4. Install spray head. 5. Complete work order data. | COMS_PLUMBER
COMS-PL-032W | 1. Turn water on and off to verify proper operation. 2. Complete work order data. | COMS_PLUMBER
COMS-PL-033S | 1. Check with opeating personnel for obvious defects. 2. Clean surface of pump with solvent. 3. Operate pump and check for leaks at pipes and connections and for excessive noise and vibration 4. Lubricate pump. 5. Check shaft alignment and clearances and pump rotation. 6. Inspect packing for leaks and tighten. 7. Tighten loose bolts and nuts; replace loose and missing hardware as needed. 8. Inspect electrical system for loose connections and frayed wires; repair as necessary. 9. Operate pump upon completion of maintenance, read and record pressure gauge readings and check discharge pressure. 10. Clean up area around pump after repairs. 11. Complete work order data. | COMS_PLUMBER
COMS-PL-035Q | 1. Inspect cleanliness, obstructions and wear. 2. Empty out the preserved water. 3. Rinse out the eyewash. 4. Refill the eyewash with potable water and preservative applicable for each type of eyewash system. 5. Complete work order data. | COMS_PLUMBER
COMS-PL-037Q | 1. Put on safety equipment prior to checking equipment. 2. Test alarm and inspect fan and sensor wiring. 3. Test detector with chlorine test kit. 4. Flush sensor unit with fresh water and drain and fill reservoir 5. Check drip rate and reservoir level in sight glass. 6. Check "O" rings; replace as required. 7. Inspect sensor mounting grommet, fan operation, detector mounting bolts and drain tube connection. 8. Check charcoal filter cartridge; replace as needed. 9. Check basket for cracked or worn areas. 10. Check detector for leaks under pressure. 11. Clean unit and surrounding area. 12. Complete work report data | COMS_WATER OPER
COMS-PL-038S | 1. Check with pump operating personnel for any obvious deficiencies. 2. Obtain and put on safety equipment for working with chemicals: goggles, apron, gloves and respirator. 3. Check oil level in pump with dipstick; add oil as necessary. 4. Inspect belt condition and tension on pump; adjust as required. 5. Flush slurry pump with fresh water. 6. Pressure test pump. 7. Inspect pump motor. 8. Operate pump and check for leaks, excessive noise and vibration. 9. Clean up area. 10. Complete work order data. | COMS_PLUMBER
COMS-PL-043A | FAA ANNUAL VALVE EXERCISING PROCEDURE Size Op Press Op Torque Max Press Max Torque Full Cycle Turn Count (in) (in psi) (in ft-lbs) (in psi) (in ft-lbs) (in revolutions) 1" NA NA 23 7 1-9 1.5" NA NA 30 9 1-9 2" 20 6 67 20 4.75-9 3" 47 14 173 52 10 4" 83 25 250 75 13-13.5 6" 117 35 367 110 19-19.5 8" 167 50 500 150 25.5-26 10" 250 75 617 185 31.5-32 12" 400 120 750 225 37.75-38 1. Locate valve using hand held GPS. 2.Check valve box, if applicable, for the following: (a) damage (document only) (b) filled w/debris (clean out) (c) paved-over (document only) 3. Remove valve box cover and locking device(s), if any, and attach portable valve exerciser to valve 4. Prior to valve exercising, verify the following historical valve data:(a) Valve Size (b) normal position (OPEN, CLOSED, LOCKED OPEN, LOCKED SHUT, throttled, etc) (c) Close Direction (CW or CCW) (d) number of turns required for full gate travel (Full Cycle Turn Count) (e) date last exercised (f) valve Op Torque (ft-lbs and psi) 5. Prior to valve exercising, verify the following valve conditions: (a) valve packing (document only) (b) packing gland nut (document only) (c) preservation condition (document only) 6. Zero the valve exerciser's revolution counter. 7. Start engine/hydraulic motor. 8. Operate hydraulic controls to ensure proper valve rotation and to control operating torque to that in (4)(f) above. NOTE: TORQUE CONTROL IS CRITICAL! The ability to control operating torque must be combined with constant monitoring of the accurate counter mechanism is paramount to the success of this procedure. 9. As the valve is turning, reduce torque setting as low as possible to turn the valve. Maintain the lowest possible torque setting throughout the turning process. NOTE: As the valve nears the CLOSED position, the initial low torque will not seat the valve. 10. When the valve moves as far as the minimum torque setting will allow, OPEN the valve approximately 3 turns and attempt to CLOSE it again at the same low torque setting. If you gain more movement from the valve as indicated on the rotation counter, repeat this step without raising torque until full gate travel is realized. 11. If full gate travel cannot be realized, then raise the operating torque by 10% and attempt another CLOSE. Repeat step (10) above.NOTE: Under NO CIRCUMSTANCES will the torque be raised by more than 50% beyond the value specified without the approval of maintenance contractor's utility manager as the risk of valve failure significantly increases. 12. If full gate travel cannot be realized, stop this procedure and document this result. 13. If full gate travel is eventually achieved, note valve stem action. If action is tight as a result of buildup on the stem threads, repeat the valve operating procedure at the minimum operating torque identified for full valve stem travel until the opening and closing actions are smooth and free. 14. Record the valve operating torques and the num | COMS_PLUMBER
COMS-PL-045S | 1. Check with opeating personnel for any deficiencies. 2. Check packing for leaks; tighten or repack as necessary. 3. Adjust impeller for optimun operation. 4. Lubricate all pump parts as required. 5. Inspect operation of discharge valve. 6. Inspect electrical system for frayed wires or loose connections; repair as necessary. 7. Check operation of controls. 8. Run pump and check for noise and vibration. 10. Complete work order data. | COMS_PLUMBER
COMS-RS-CUP-001A | 1. Prepare for, schedule, and coordinate annual boiler and unfired pressure vessel inspection and testing as required by the State of New Jersey during the month of September. 2. Notify the COR ten (10) working days prior to the State Inspection visit. 3. In the event of a failed inspection the Contractor must notify the COR within one (1) working day. 4. Provide report(s) documenting inspections. | COMS_CUP OPER
COMS-RS-CUP-002A | 1. Perform annual boiler combustion adjustments and reporting in accordance with New Jersey Administrative Code 7:27-19.16. 2. Perform annual exhaust gas analyzer (EGA) inspection and calibration per manufacturer's recommendations. | COMS_CUP OPER
COMS-RS-CUP-004S | 1. Provide detailed schedule of work to the COR prior to start of work. 2. Perform system check, verifying proper system operation, communication, and calibration 3. Provide report(s) for each day of work performed, including points/systems checked and any issues identified for correction. | COMS_CUP OPER
COMS-RS-CUP-006A | 1. Calibrate balometer using factory authorized distributor. 2. Use of another company for calibration must be approved by the COR in writing no later than December each year. 3. Provide calibration report. | COMS_CUP OPER
COMS-RS-CUP-007A | 1. Calibrate the refrigerant storage tank scale during the month of June. 2. Affix a label to the scale identifying the date of last calibration. 3. Provide calibration report. | COMS_CUP OPER
COMS-RS-ELEC-01A | Utility line tree trimming is to be performed during October and November. 1. Cut back branches that overhang or grow into power lines and communications lines. 2. Cut back branches which are at risk of falling on power lines and communication lines during storms or heavy winds. 3. Shape the entire tree rather than notch the top. Branch stubs are not permitted. All branches must be pruned back to the next major limb or to the tree trunk. Pruning cut must be performed in a manner which leaves the branch collar exposed (with no stub beyond the branch collar). 4. If required, remove the entire tree. | COMS_ELEC-LINE
COMS-RS-ENV-002A | 1. Add instructed amount of fuel additive for water and sludge treatment to storage tank. Treatment instructions must be followed for the correct ratio. 2. Close tank and record treatment type and amount used. | COMS_ENV SPEC
COMS-RS-ENV-002M | The Contractor must perform the following inspection activities for FAA-owned product storage, waste holding and spill containment tank systems on a monthly basis: 1. Monitor and record primary tank level in both inches and gallons using the appropriate tank chart. If water is detected, note presence and record water level. 2. Inspect vault space (if applicable) for presence of liquid. If present, record liquid level in both inches and gallons. 3. Inspect interstitial space (if applicable) for presence of liquid. If present, record liquid level in both inches and gallons. 4. Visually inspect the tank's condition and note the conditions of the following as appliicable to the tank system: (a) liquid level gauge (b) spill bucket/leak collection sump (c) fill connection spill containment sump (d) fill cap securely in place (e) fill ports (clear and free of obstructions?) (f) vent riser and cap (g) tank exterior (h) labels (i) aboveground piping (j) filling platform, walkway and/or stairs (k) tank supports (l) foundation 5. Record unsatisfactory conditions, evidence of spill or leaks, and corrective actions in the comments. 6. Complete work order data, attach to WR, and email TE-II-13-13 to COR and Environmental POC. | COMS_ENV SPEC
COMS-RS-ENV-002S | 1. If possible, perform PM prior to refilling tank. 2. Apply water detecting paste to fuel level stick as directed by paste manufacturer. 3. Stick tank with paste applied to determine if water is present. 4. If water is present, remove and dispose of all water content within storage tank. 5. Stick tank again to ensure all water has been removed from tank. 6. If small amount of water remains, apply water absorbing polymer to absorb remaining water from tank. 7. Record findings and fuel level. | COMS_ENV SPEC
COMS-RS-ENV-002W | 1. Monitor and record tank level and vault level in both inches and gallons. | COMS_ENV SPEC
COMS-RS-ENV-003M | 1. Visually inspect and record the condition of the hazardous waste satellite accumulation site. 2. Ensure oily waste/rags are not mixed with any hazardous waste. 3. Check containers for proper labeling, condition, and secondary containment. 4. Complete work order data, submit report, and email to COR. | COMS_ENV SPEC
COMS-RS-ENV-004M | Submit the following documents by the 5th of each month with complete and accurate data from the previous month: 1. Refrigerant Service Order Forms 2. Refrigerant Inventory Control Logs 3. Refrigerant Purchase, Use, Disposal Reports | COMS_ENV SPEC
COMS-RS-ENV-005S | Perform the following as part of the refrigerant (ODS) compliance audit: 1. Review documentation of all work performed on ODS containing appliances during the previous year. 2. Verify refrigerant cylinder inventory. 3. Document the results by submitting a cylinder audit report and an audit discrepancy correction report, if necessary. | COMS_ENV SPEC
COMS-RS-ENV-006A | The Contractor must perform annual certification of Veeder-Root systems connected to FAA-owned ASTs (annual certification of UST Veeder-Root systems is covered under COMS-RS-ENV-009A). The annual certifcation must include the following actions: 1. Test the electronic and mechanical components of AST systems. The electronic and mechanical components may include the following as applicable to the AST system: • Automatic tank gauges; • Probes and sensors; • Automatic line leak detectors; 2. Prepare an Annual Veeder-Root Certification Report that documents the results of #1 above. The report should include the following information, as applicable to the AST Veeder-Root system: • Indicate if Automatic Tank Guaging (ATG) is functioning properly. • Indicate if Interstital Monitor is functioning properly. • Indicate if Leak Detection is functioning properly (i.e. do leak tests pass?). • Indicate if probes are functioning properly (i.e. do fuel/water levels match probe readings?). • Indicate if alarms are functioning properly (i.e. do alarms trip when tested?). • Indicate if probes/alarms are in good condition based on visual observation. • Indicate if sensors are functioning properly (i.e. do sensors trip and clear when tested?). • Indicate if sensors are programmed appropriately. • Describe system/equipment failures, or indicate if there were none. • Describe any corrective actions taken, or indicate if there were none. The Contractor must submit the annual Veeder-Root certification report to the COR and Environmental POC within thirty (30) days or less from the completion of the last certification test. | COMS_ENV SPEC
COMS-RS-ENV-006M | The Contractor must submit a monthly Veeder-Root summary report to the COR and Environmental POC by the 7th of each month. The report must be prepared for Veeder-Root systems connected to FAA-owned USTs and ASTs. The report must include the following information: 1. Describe maintenance activities performed on the system during the reporting period, or indicate if none occurred. 2. Describe major equipment failures and associated corrective actions that occured with the sysetm during the reporting period, or indicate if none occurred. 3. Describe system upgrades that occurred during the reporting period, or indicate if none occurred. 4. Indicate whether any maintenance activities, system upgrades or corrective actions were performed by a subcontractor during the reporting period. Record the name of the subcontractor and the scope of work they performed on the system. 5. Complete monitoring logs for each system. 6. Attach copies of environmental compliance reports printed from the Veeder-Root system. This should include ATG test results, leak test results, and liquid sensor status reports, as applicable. | COMS_ENV SPEC
COMS-RS-ENV-009A | The Contractor must perform the following inspection and testing activities for FAA-owned UST systems on an annual basis: 1. Perform an annual walkthrough of the UST systems, including day tanks fed by USTs, that includes the following actions: • Open and visually check each containment device/sump for damage, leaks to the containment area, or releases to the environment; remove any liquid or debris from each containment device, and properly dispose of any substances collected; check each double walled containment device with interstitial monitoring for leaks in the interstitial area; • Open and visually check each dispenser cabinet for damage, leaks to the containment area or releases to the environment, remove any liquid or debris from each containment device, and properly dispose of any substances collected; check each under-dispenser containment device with interstitial monitoring for leaks in the interstitial area; and • Check devices such as tank gauge sticks or ground water bailers for operability and serviceability. 2. Test the electronic and mechanical components of UST systems, including day tanks fed by USTs. The electronic and mechanical components may include the following as applicable to the UST system: • Automatic tank gauges; • Probes and sensors; • Automatic line leak detectors; • Vacuum pumps and pressure gauges, and • Handheld electronic sampling equipment associated with groundwater and vapor monitoring. 3. Prepare an annual inspection report that documents the following information as applicable to the UST system: • Identify areas inspected; • Whether each area was acceptable, or required corrective action; • A description of any corrective actions taken, and • Delivery records if spill prevention equipment is checked less than every 30 days due to infrequent deliveries. • For automatic UST monitoring systems (i.e. Veeder-Root): • Indicate if Automatic Tank Guaging (ATG) is functioning properly. • Indicate if Interstital Monitor is functioning properly. • Indicate if Leak Detection is functioning properly (i.e. do leak tests pass?). • Indicate if probes are functioning properly (i.e. do fuel/water levels match probe readings?). • Indicate if alarms are functioning properly (i.e. do alarms trip when tested?). • Indicate if probes/alarms are in good condition based on visual observation. • Indicate if sensors are functioning properly (i.e. do sensors trip and clear when tested?). • Indicate if sensors are programmed appropriately. • Describe system/equipment failures, or indicate if there were none. • Describe any corrective actions taken, or indicate if there were none. The Contractor must submit documentation of the annual UST inspection and testing to the COR and Environmental POC within thirty (30) days or less from the date inspection and testing activities are completed. | COMS_ENV SPEC
COMS-RS-ENV-009O | The Contractor must perform the following inspection and testing activities for FAA-owned UST systems every (3) years: 1. Integrity testing of UST system containment devices where interstitial monitoring of piping is performed; 2. Tightness testing of spill prevention equipment (i.e. containment sumps, catchment basins, spill buckets), and 3. Inspection of overfill prevention equipment (i.e. automatic shutoff devices/flapper valves, overfill alarms, ball float valves). The Contractor must submit the triennial UST inspection and testing report to the COR and Environmental POC within thirty (30) days or less from the date inspection and testing activities are completed. | COMS_ENV SPEC
COMS-RS-ENV-011M | Submit monthly inspection report that details the inspections of concrete/curbed containment areas after each rain event as well as actions taken including checking for sheen or oil, open valve if clean, and then closing valve after water has drained. Report format is showin in Technical Exhibit II-13-11 (Containment Area Inspection Log). | COMS_ENV SPEC
COMS-RS-ENV-012M | Submit the following reports by the 15th of each month: 1. Report the amount (weight or volume) of recycled items (batteries, fuel, used oil, florescent tubes). Report format is listed in Technical Exhibit II-13-8 (Report of Universal Waste). 2. Report all solid waste and recycled material that is removed from the Technical Center. Report format is listed in Technical Exhibit II-13-9 (Technical Center Solid Waste and Recycling Report). | COMS_ENV SPEC
COMS-RS-ENV-013Q | 1. Provide manufacturer-recommended maintenance, including adding and removing solvent. 2. Attach documentation of services provided and waste removed to the work request. | COMS_ENV SPEC
COMS-RS-FP-001A | 1. Inspect all buildings for fire and smoke barrier violations following ASTM International standards as described in ASTM 2174 and ASTM 2393. Inspections are to include ASTM Standards 2174 and 2393 smoke barrier and through penetration fire safety of ceiling and wall assemblies. 2. Provide written report including violations. | COMS_FIRE INSPEC
COMS-RS-FP-002A | 1. Provide schedule for occupied buildings to Safety Office for Prioritization. 2. Once schedule is approved by Safety Office, conduct fire drills. 3. Initiate corrective action upon discovery of discrepancies, regulation and code violations. 4. Document findings on RS work request. | COMS_FIRE INSPEC
COMS-RS-FP-003M | 1. Witness Daycare personnel conducting fire drill. 2. Check emergency light operation. 3. Perform inspection of Daycare area for code violations. 4. Initiate appropriate action for steps 2 and 3. 5. Document performance of fire drill and any actions taken for steps 2 and 3. | COMS_FIRE INSPEC
COMS-RS-FP-006A | 1. Coordinate with fire inspectors to take the fire suppression system offline. 2. Precautions must be taken by contractor around asbestos dampers on all hood systems. 3. Remove fire suppression system and throughly degrease and clean all parts. 4. Apply chemical cleaner/degreaser to all areas including but not limited to - All ductwork between hood and exhaust - Fan housing - Fan blades and fan enclosure - Hood area and plenums - Filter trays - Fire suppression nozzles including all cabling for suppression system - Dry hood area - Light fixtures 5. Once cleaner/degreaser is sprayed, all parts must be cleaned of all grease and residue. 6. Ensure that all chemical residue has been removed. 7. Reinstall all fire supression parts and ensure proper reinstallation. 8. Test fire suppresion system to ensure proper function. 9. Take time stamped photos before and after cleaning showing all ducts and components listed above. Each photo must be labeled with identification and location information. | COMS_FIRE INSPEC
COMS-RS-FP-006S | 1. Coordinate with fire inspectors to take the fire suppression system offline. 2. Precautions must be taken by contractor around asbestos dampers on all hood systems. 3. Remove fire suppression system and throughly degrease and clean all parts. 4. Apply chemical cleaner/degreaser to all areas including but not limited to - All ductwork between hood and exhaust - Fan housing - Fan blades and fan enclosure - Hood area and plenums - Filter trays - Fire suppression nozzles including all cabling for suppression system - Dry hood area - Light fixtures 5. Once cleaner/degreaser is sprayed, all parts must be cleaned of all grease and residue. 6. Ensure that all chemical residue has been removed. 7. Reinstall all fire supression parts and ensure proper reinstallation. 8. Test fire suppresion system to ensure proper function. 9. Take time stamped photos before and after cleaning showing all ducts and components listed above. Each photo must be labeled with identification and location information. | COMS_FIRE INSPEC
COMS-RS-GEV-037A | 1. Add instructed amount of fuel additive for water and sludge treatment to storage tank (associated with generator). Treatment instructions must be followed for the correct ratio. 2. Close tank and record treatment type and amount used on PM. | COMS_EQUIP MECH
COMS-RS-GEV-037S | 1. If possible, perform PM prior to refilling tank (associated with generator). 2. Apply water detecting paste to fuel level stick as directed by paste manufacturer. 3. Stick tank with paste applied to determine if water is present. 4. If water is present, remove and dispose of all water content within storage tank. 5. Stick tank again to ensure all water has been removed from tank. 6. If small amount of water remains, apply water absorbing polymer to absorb remaining water from tank. 7. Record findings and fuel level on PM. | COMS_EQUIP MECH
COMS-RS-IE-001S | 1. Clean floors and equipment exteriors in mechanical / electrical room. 2. Dispose of trash and other items, as appropriate, with proper approval from COR if items do not belong to Contractor. | COMS_GEN MAINT
COMS-RS-IE-002S | 1. Clean surfaces with power washer as follows: (a) B300 main entrance (Parking Lot A) concrete surfaces and pavers (b) B300 & B316 entrance / patio (Parking Lot B-1) concrete surfaces including columns, walls, and steps (c) B300 Loading dock entrance concrete surfaces including steps, loading dock wall, sidewalk (d) B320 entrance (e) B305 entrance | COMS_LABORER
COMS-RS-PL-001M | 1. Provide enzyme treatment for the sanitary lines for the cafeteria in Buildings 300 and Building 301 monthly. There are currently four (4) floor drains that lead to the sanitary lines in building 300 and one (1) floor drain that leads into the sanitary lines in Building 301 cafeteria. 2. All lines must be clear and free flowing. | COMS_PLUMBER
COMS-RS-PL-002M | 1. Flush all potable and domestic water (hot and cold) at all points of use. This includes locations/applications such as water fountains, kitchenette sink faucets, bathroom sinks, glass fillers, shop and slop sinks, showers, and plumbed eye wash stations. a. Flush time will vary from 10 to 30 minutes based upon distance from entry point to the building. So the bottom floor in a multi floor building will be flushed the longest (minimum of 30 minutes, 2nd floor 25 minutes, 3rd floor 20 minutes and so on). b. Flushing may need to be done in a phased or zoned approach to ensure pressure remains sufficient. c. Point of use charcoal filters will remain off where the application allows for that fixture to run without a filter present (ex. most water fountains). 2. Remove all accessible aerators and point of use filters (floor by floor) before flushing begins. 3. Cold water will be flushed first followed by hot water. Ensure each hot water heater or source is at maximum temperature and flush the hot system running hot until maximum temperature is reached at farthest tap. 4. Flush each toilet in each bathroom. 5. Water using devices such as dishwashers, plumbed coffee pots, ice makers/machines, will need to be cleaned, emptied, and flushed per the manufacturers maintenance instructions. 6. When flushing of each area or zone is complete, clean and then reinstall each aerator. Cleaning will consist of rinsing aerator out so no debris/material is present and then spraying with a bleach water solution. 7. If showers are present, spray all showerheads with the same bleach water solution. Inform federal COM’s personnel, the treatment plant operator, and the Water System Program Manager of the intended schedule prior to starting work. Complete Work Order Data. | COMS_PLUMBER
COMS-RS-PL-002S | At the start of each step, all valves are assumed open. Refer to map provided titled, "Flushing Procedure New Waterline" for details on locations of valves and hydrants. 1. Flush from Building 33 to T&A Side. Flush approximately 18,000 gallons from PWH-S-004. 2. Flush from Main Gate to Fire House (Building 302). Isolate Service Road. Shut off Valve PWV-038. Shut off loop feed by Building 301. Shut off valve PWV-033. Flush approximately 12,000 gallons from PWH-S-007 by Building 302. 3. Flush from Main Gate to Building 303. Isolate Service Road. Shut off valve PWV-038. Shut off loop feed by Parking Lot K. Shut off valve PWV-011. Flush approximately 8,000 gallons from PWVH-G-003 by Building 303. 4. Flush from Service Road connection to Building 303. Shut off valve PWV-042. Flush approximately 4,000 gallons from PWH-G-003 by Building 303. 5. Flush from Parking Lot K to Parking Lot G. Shut off valve PWV-027. Flush approximately 15,000 gallons from PWH-G-009 by Building 360. 6. Flush from Building 301 to Parking Lot G. Shut off valve PWV-025. Flush approximately 6,000 gallons from PWH-G-009 by Building 360. Flush Hydrants (see map provided for detailed locations) Ground Level Type Hydrant (Green Sprinkler Box): PWH-G-001 PWH-G-002 PWH-G-003 PWH-G-004 PWH-G-005 PWH-G-006 PWH-G-007 PWH-G-008 PWH-G-009 PWH-G-010 PWH-G-011 Stand Pipe Type Hydrant PWH-S-001 PWH-S-002 PWH-S-003 PWH-S-004 PWH-S-005 PWH-S-006 PWH-S-007 PWH-S-008 PWH-S-009 PWH-S-010 Complete work order data as required. | COMS_PLUMBER
COMS-RS-RD-001M | 1. Sweep asphalt roads, concrete roads, and paved parking areas as identified on Technical Exhibit II-14-1. Surfaces must be free of sand, sediment, broken glass, debris, and other materials. | COMS_HEAVY EQUIP
COMS-RS-SU-002M | 1. Read sewage flow meter. 2. Document meter amounts and report to FAA-designated personnel. Report format is shown in Technical Exhibit II-2-1 (Monthly Wastewater Meter Readings). | COMS_WATER OPER
COMS-RS-SU-002Q | 1. Calibrate sewage flow meter. 2. Attach calibration report to PM. | COMS_WATER OPER
COMS-RS-SU-003M | 1. Read water meters. 2. Report findings to the COTR. 3. Complete Work Order Data. | COMS_WATER OPER
COMS-RS-SU-003O | 1. Calibrate diversion source flow meters to within 5% accuracy. | COMS_WATER OPER
COMS-RS-WTP-001W | Seven (7) weekly sampling points will be chosen by the licensed Water Treatment Plant Operator as representative of domestic water. Samples must be taken at the following locations for Weekly Sampling: • One (1) total coliform sample must be taken from untreated well water supply on a rotating basis from Wells 1R, 2R, and 5. • Three (3) separate samples must be taken on a weekly rotating basis from three (3) of twenty-nine (29) designated cold water sampling taps in the Technical Center’s water distribution system for total coliform analysis and chlorine disinfectant residual field testing. The locations of the sampling taps are B300 LFA, B300 Cafe, B300 MS, B300 3 J18, B300 2 J24, B300 4DS, B316 2 BR, B316 4BR, B316 3 BR, B301 2 OPS, B301 MOD, B305, B306, B303, B296, B201, B275, B292, B210, B204, B203, B270, B27, B28, B56, B214, B277, B211, and B350. • One (1) sample must be collected from the Building 208 domestic water system, when operable for total Coliform analysis and chlorine disinfectant residual field testing. • One (1) sample must be collected from Building 33 domestic water system at the point of entry for total Coliform analysis and chlorine disinfectant residual field testing. All reports are to be attached to the completed Recurring Services Work Request. | COMS_WATER OPER
COMS-RS-WTP-002M | Samples must be taken at the following locations for Monthly Sampling: • One (1) total Coliform sample must be collected from the Building 305 EOF domestic water system. • Twenty four (24) Chlorine samples must be collected (form BSDW-25) at locations as determined by licensed Water Treatment Plant Operator. All reports are to be attached to the completed Recurring Services Work Request. | COMS_WATER OPER
COMS-RS-WTP-003O | Testing must be performed twice a month for the North and South Side Fire Tanks for Chlorides, PH, Conductivity and Temperature for a total of 8 tests per month (four tests per month on each of the two tanks). All reports are to be attached to the completed Recurring Services Work Request. | COMS_WATER OPER
COMS-RS-WTP-005A | Samples must be taken at the following locations for Annual sampling: • One (1) sample at Building 33 point of entry for contaminant Nitrate (as N). • One (1) sample at Building 33 point of entry for secondary Contaminants. Between 1 January and 30 September • One (1) sample @ point of entry for inorganics. • One (1) sample for chloride at each of 5 locations including wells 1R, 2R, 3, 5, and 11 in the 3rd quarter of each year (NJDEP Preprint Quarterly Diversion Report). • One (1) sample for Trihalomethanes @ Haloacetic acids from (2) locations with the maximum residence time from the WTP during the warmest water temperature. Collections must take place during the period of July 1 to September 30 . • At Building 33 one (1) sample at point of entry for volatile organics (state and federal) from April 1st to June 30th. • One (1) lead and copper sample at each of 10 Buildings located in the Building 33 distribution system. Sample must be collected Between June 1st and September 30th. All reports are to be attached to the completed Recurring Services Work Request. | COMS_WATER OPER
COMS-RS-WTP-008M | Complete the Monthly Operating Report of T2 Water Treatment Plant (BSDW-40) with accompanying correspondence. Submit to the COR five (5) days prior to the date that reports must submitted to the NJDEP. | COMS_WATER OPER
COMS-RS-WTP-010Q | Complete the Quarterly Water Diversion Report (NJDEP Pre-Printed Form) with accompanying correspondence. Submit to the COR five (5) days prior to the date that reports must submitted to the NJDEP. | COMS_WATER OPER
COMS-RS-WTP-011M | Complete the following forms and submit to the COR on the first working day of each month: • Water Treatment Plant Daily Checks • Water Treatment Plant Operating Record • Monthly Coliform Summary Report • Monthly Operating Report for Groundwater Treatment Plants • Monthly Chemical Use Record • Monthly Well Use Record • Monthly Water Production • Monthly Water Quality Tests • Monthly Operating Data Sheet for Building 208 • Monthly Firewater Tank Testing • Monthly Water and Sewer Meter Readings | COMS_WATER OPER
COMS-RS-WTP-012Q | Complete the Disinfectant Residuals Reporting Form (BSDW-25) and submit to the COR on the first working day of each calendar quarter: | COMS_WATER OPER
COMS-RS-WTP-015Q | 1. Analyze a water sample from the point of entry into our water distribution system and a raw water sample from Well 2R for aluminum. | COMS_WATER OPER
COMS-RS-WTP-016Q | Analyze collected water samples quarterly beginning the first of the calendar year from pre-determined points of entry for the following analytes: Perfluorononanoic acid (PFNA), 1,2,3-Trichloropropane (TCP), ethylene dibromide (EDB) and dibromochloropropane (DBCP). The quarterly sampling will also measure for the following radioactivity measurements: gross alpha particle activity (including radium-226 but excluding radon and uranium), combined radium-226 and radium-228, and uranium. Sampling points will be chosen by the licensed Water Treatment Plant Operator as representative of domestic water. All reports are to be attached to the completed Recurring Services Work Request | COMS_WATER OPER
COMS-SU-001S | 1. Inspect and clean all existing storm drains, catch basins, drop inlets, and similar structures on a regular schedule based on the rate of silting or clogging of debris to insure proper run-off. 2. Report findings to the COTR. 3. Complete Work Order Data. | COMS_LABORER
COMS-SU-005W | 1. Inspect exterior and interior for structual deficiencies 2. Inspect pumps/piping equipment for leaks, spills and damage 3. Inspect for proper operation of pumps and equipment 4. Perform operational testing on operating wells 5. Report any deficiencies | COMS_WATER OPER
COMS-SU-007S | 1. Locate MH byr ARH Maps 2. Verify location and paint # if needed 3. Inspect manhole for any structural defects and note descrepancies 4. Inspect for any blockages, debris, low flow etc. 5. Remove debris or clear blockage as needed 6. Note any damage, obstructions,debris,blockages on inspection form | COMS_LABORER
COMS-SU-011M | 1. Inspect septic tank areas and leech fields. 2. When accessible, inspect internally. 3.Treat septic system with 2 oz. of Bioguard Plus (or equivalent) septic drain cleaner poured into one building toilet and then flushed. | COMS_PLUMBER
COMS-SU-011O | 1. Clean out sludge and scum from septic system. 2. Inspect interior of system including distribution box, report deficiencies. 3. Ensure lid and soil are replaced. | COMS_PLUMBER
COMS-SU-012O | 1.Exercise gas valves on the load side of gas meters in the 3rd year of the Contract, between May 1 and August 31. 2. Ensure after exercising the gas valves that all natural gas equipment / systems are back in safe operation. | COMS_PLUMBER
COMS-WTP-001M | 1. Search for leaks by inspection of water levels and visual inspection of all pipes and containment walls. 2. Inspect for visible oily sheens at discharge pipes and on the discharge side of treatment works. Inspect for any spill or signs of hazardous substance or waste. Whenever a visible oily sheen on the discharge side of the treatment works is observed, notify COR or FAA-designated personnel as soon as possible. 3. Inspect for sediment buildup and debris in draw off at the inlet and outlet pipes and in the treatment works. If sediment or debris is found, notification of the COR is required as soon as possible. 4. As needed, remove water from oil/water separators and pump out units. Ensure that separators are refilled with water to the proper level after pumping out the unit. | COMS_WATER OPER
COMS-WTP-001S | **Note: Semiannual PM must be performed in conjunction with Monthly PM 1. Conduct routine operational cleaning including the removal of all sediments and debris and a thorough washing of treatment works. | COMS_WATER OPER
COMS-WTP-016Q | 1. Check with operating or area personnel for any deficiencies. 2. Check operation of mixer for excessive noise and vibrations; align or adjust as required. 3. Clean machine thoroughly of dust, and dirt particles. 4. Check motor, switches, controls and motor bearings for overheating.. 5. Check anchor bolts for tightness; tighten as required. 6. Complete work report data. | COMS_WATER OPER
CS-ASTAIR-001M | 1. Secure stairs to prevent any traffic during shampooing. 2. Vacuum atrium stairs and landings. 3. Apply approved carpet cleaning solution. 4. Use rotary scrub machine to clean. Repeat Step 3 to ensure proper cleaning. 5. Let Dry. 6. Vacuum carpet to remove any powder residue. Note: A Carpet extraction method may be used when approved. | CUST_JANITOR
CS-BLCKBB-001A | 1. Dust top ridge of black tile baseboard. 2. Spray baseboard with an approved cleaning solution. 3. Wipe with a dry cloth to remove all dirt, streaks, spots, and residue. | CUST_JANITOR
CS-BLUEWALL-001A | 1. Dust tops of all blue wall wooden surfaces. 2. Use window cleaning solution and use squeegee to remove dirt and grime. 3. Wipe with a dry cloth all drips, splashes, and residue from cleaning. | CUST_JANITOR
CS-BREAKRM-001S | 1. Unplug the unit and defrost freezer. 2. Empty and discard any items left inside of the Unit. 3. Thoroughly clean and disinfect inside of entire refrigerator with approved cleaning product. 4. Pull unit away from the wall and clean floor underneath. 5. Clean outside of the unit with approved cleaning product. 6. Vacuum coils in rear of refrigerator and move the unit back to the wall and plug it in. 7. Clean all door gaskets to ensure proper seal. 8. Replace box of baking soda to absorb odors inside of refrigerator. 9. Note any deficiencies, door seals loose doors etc... and if needed enter a work request to address any further issues. | CUST_JANITOR
CS-BREAKRM-002M | 1. With a wet melamine-type sponge, wipe cabinet and countertops thoroughly. Ensure that all dirt, dust and debris are removed. 2. Rinse & wipe clean with dry micro-fiber cloth. | CUST_JANITOR
CS-BREAKRM-002Q | 1. With a wet melamine-type sponge, wipe cabinet and countertops thoroughly. Ensure that all dirt, dust and debris are removed. 2. Rinse & wipe clean with dry micro-fiber cloth. | CUST_JANITOR
CS-BREAKRM-003W | 1. Spray cleaning solution on a microfiber cloth and wipe the exterior of the appliance from the top down removing all dirt ,splatters etc... 2. Rinse with a wet cloth. 3. With a dry microfiber cloth wipe the appliance dry and leave the appliance streak free. | CUST_JANITOR
CS-BUFLOOR-001W | 1. Vacuum entire floor. 2. Mop entire floor. 3. Spray floor with approved buffing solution just before buffing. 4. Machine buff floor leaving a shine with no streaks or residue. | CUST_JANITOR
CS-BUFVCT-001M | 1. Vacuum entire floor. 2. Mop entire floor. 3. Spray floor with approved buffing solution just before buffing. 4. Machine buff floor at 175-300 rpm leaving a shine with no streaks or residue. | CUST_JANITOR
CS-BUFVCT-001Q | 1. Vacuum entire floor. 2. Mop entire floor. 3. Spray floor with approved buffing solution just before buffing. 4. Machine buff floor at 175-300 rpm leaving a shine with no streaks or residue. | CUST_JANITOR
CS-BUFVCT-001W | 1. Vacuum entire floor. 2. Mop entire floor. 3. Spray floor with approved buffing solution just before buffing. 4. Machine buff floor at 175-300 rpm leaving a shine with no streaks or residue. | CUST_JANITOR
CS-CLEANFLR-001W | 1. Machine sweep floor. | CUST_JANITOR
CS-CUBECLN-001A | 1. Starting at the top, dust off the tops of cabinets, walls and work surfaces with a microfiber dust cloth. 2. Spray disinfectant on damp microfiber cloth and wipe down cabinet tops, cabinet doors and work surfaces. 3. Wipe dry with clean cloth. 4. Vacuum and shampoo carpet. | CUST_JANITOR
CS-CUBECLN-001Q | 1. Starting at the top, dust off top of cabinets, walls and work surfaces with a microfiber dust cloth. 2. Vacuum carpet and all debris from surrounding area. 3. Spray disinfectant on damp microfiber cloth and wipe down cabinet tops, cabinet doors and work surfaces. 4. Wipe dry with clean cloth. | CUST_JANITOR
CS-DBACKHAL-001M | 1. Use a microfiber duster or a treated duster. 2. Remove all dirt, dust, cobwebs, and other foreign matter from all exposed surfaces. | CUST_JANITOR
CS-DBLIND-001A | 1. Close blinds. 2. Dust blinds with a microfiber duster or a treated duster to remove all dust and debris. 3. Repeat on both sides of the blinds until completed. 4. Ensure that all dust is created/moved around is removed from windows and ledges. | CUST_JANITOR
CS-DBLIND-001S | 1. Close blinds. 2. Dust blinds with a microfiber duster or a treated duster to remove all dust and debris. 3. Repeat on both sides of the blinds until completed. 4. Ensure that all dust is created/moved around is removed from windows and ledges. | CUST_JANITOR
CS-DCAFEHTR-001M | 1. Dust top of the heater units with a microfiber duster or vacuum brush attachment. 2. Clean entire area underneath the heater units with a microfiber duster or vacuum to remove all dirt and debris. | CUST_JANITOR
CS-DHIGH-001Q | 1 Use a microfiber duster or a treated duster with an extension pole to dust and remove all cobwebs, dust, and debris. 2. Clean surrounding area of fallen debris. | CUST_JANITOR
CS-DOCKLIFT-001M | 1. Secure area. 2. Raise the lift. 3. Using a long-handled broom, remove all debris under the lift and discard. 4. Return lift to operating position. 5. Repeat Step 1 through Step 4 for each lift. | CUST_JANITOR
CS-DRYMOP-001W | 1. Dry mop the floor with a completely dry microfiber mop. 2. Ensure no dirt or debris is left behind. | CUST_JANITOR
CS-DSTAGE-001M | 1. Sweep with a pan and broom entrire area to remove large debris. 2. Dust mop entire wooden stage with a microfiber dust mop. 3. Remove all debris and tape from floor. | CUST_JANITOR
CS-DUST-001B | 1. General dusting with a microfiber duster or a treated duster (including but not limited to pictures, displays, bookcases, statues, ledges, and window sills) 2. Ensure that all dust created/moved around is removed from surrounding surfaces. | CUST_JANITOR
CS-DUST-001M | 1. General dusting with a microfiber duster or a treated duster (including but not limited to pictures, displays, bookcases, statues, ledges, and window sills) 2. Ensure that all dust created/moved around is removed from surrounding surfaces. | CUST_JANITOR
CS-DUST-001W | 1. General dusting with a microfiber duster or a treated duster (including but not limited to pictures, displays, bookcases, statues, ledges, and window sills) 2. Ensure that all dust created/moved around is removed from surrounding surfaces. | CUST_JANITOR
CS-DUSTPLNE-001A | 1. Block off work area around the atrium under the airplane. 2. With a lift dust airplane with a microfiber dust cloth and extension pole clean the airplane surfaces. 3. Clean entire floor area under the plane to remove fallen dust. 4. Restore access to the area. | CUST_JANITOR
CS-ELEVATOR-001M | 1. Call security to take elevator out of service 2. Remove and dust the light diffuser where applicable,clean and rinse diffuser and wipe dry. 3. Dust elevator vents ensure all debris,dust & cobwebs are removed. 4. Use an approved cleaning solution and microfiber cloth to ensure proper cleaning is achieved. 5. Reinstall the light diffuser. 6. Dust and using an approved disinfectant wash all hard surface walls, railings control panels and both sides of doors on all floors . Wipe dry and free of smears, streaks and smudges. 7. Polish and buff all stainless steel to shine on both sides of the elevator doors on each floor. Ensure it is not left greasy. 8. Vacuum elevator floor (where applicable mop and allow to dry). 9. Apply an approved carpet cleaning solution. 10. Use rotary scrub machine to clean and let carpet dry (when approved carpet extraction method may be used). 11. Vacuum carpet again to remove any carpet residue. 12. Vacuum elevator tracks on all floors to remove all loose dirt. 13. Call security to place the elevator back in service | CUST_JANITOR
CS-FURN-001M | 1. Vacuum all upholstery furniture with upholstery brush and crevis attachments. 2. Wipe down all furniture with a cleaning cloth and approved cleaning solution. | CUST_JANITOR
CS-FURN-001Q | 1. Vacuum all upholstery furniture with upholstery brush and crevis attachments. 2. Wipe down all furniture with a cleaning cloth and approved cleaning solution. | CUST_JANITOR
CS-GLBWALL-001S | 1. Spray with approved window cleaning solution. 2. Dry with a microfiber cloth or squeegee and repeat to clean other side of wall area. 3. Ensure there are no streaks, residue, or smudges, etc. 4. Ensure that all debris, tape, and glue residue have been removed. 5. Repeat Steps for each side of glass wall area. | CUST_JANITOR
CS-GLDOOR-001W | 1. Spray with approved glass cleaning solution. 2. Dry with a microfiber cloth or squeegee. 3. Ensure there are no streaks, residue, or smudges, etc. 4. Ensure that all debris, tape, and glue residue have been removed. 5. Repeat all steps for both sides of glass | CUST_JANITOR
CS-GLRAIL-001S | 1. Dust handrail. 2. Spray glass with approved window cleaning solution. 3. Dry with a microfiber cloth or squeegee. 4. Ensure there are no streaks, residue, or smudges, etc. 5. Ensure that all debris, tape, and glue residue have been removed. 6. Repeat Steps 2-5 for each side of handrail. 7. Spray approved stainless steel cleaner/polish on cleaning cloth. 8. Wipe stainless steel outer edge of handrail with cleaning cloth. 9. Ensure stainless steel is free of streaks and residue. | CUST_JANITOR
CS-GLWALL-001M | 1. Spray with approved window cleaning solution. 2. Dry with a microfiber cloth or squeegee. 3. Ensure there are no streaks, residue, or smudges, etc. 4. Ensure that all debris, tape, and glue residue have been removed. 5. Repeat all steps for both sides of glass. | CUST_JANITOR
CS-GLWALL-001Q | 1. Spray with approved window cleaning solution. 2. Dry with a microfiber cloth or squeegee. 3. Ensure there are no streaks, residue, or smudges, etc. 4. Ensure that all debris, tape, and glue residue have been removed. 5. Repeat all steps for both sides of glass. | CUST_JANITOR
CS-GLWALL-001W | 1. Spray with approved window cleaning solution. 2. Dry with a microfiber cloth or squeegee. 3. Ensure there are no streaks, residue, or smudges, etc. 4. Ensure that all debris, tape, and glue residue have been removed. 5. Repeat all steps for both sides of glass. | CUST_JANITOR
CS-GRIPFLR-001A | 1. Vacuum area or section of the floor. 2. Mop the area or section of the floor. 3. Place wet floor signs and cones to block off the area. 4. Apply DE-51 Grip Master to the Area or section of the floor with a pump sprayer. 5. Spread evenly and agitate with a damp mop. 6. Allow to completely dry. 7. Remove signs and cones. | CUST_JANITOR
CS-HANDRAIL-001M | 1. Get a spray bottle and fill with an approved disinfectant solution. 2. Spray disinfectant solution on handrails and support rails. 3. Scrub clean. 4. Ensure that all dirt, dust, and debris are removed. | CUST_JANITOR
CS-HANDRAIL-001W | 1. Get a spray bottle and fill with an approved disinfectant solution. 2. Spray disinfectant solution on handrails and support rails. 3. Scrub clean. 4. Ensure that all dirt, dust, and debris are removed. | CUST_JANITOR
CS-HANDSANI-001Q | 1.Check the product level and replace with new if needed. 2. Check the product expiration date, replace if expired. 3. Check dispenser is in good operational conditioning. 4. Check batteries and change if needed. | CUST_JANITOR
CS-LOCKER-001W | 1. Starting at the top, dust off outside of lockers with a microfiber dust cloth, including locker doors. 2. Clean all debris from surrounding area. 3. Spray disinfectant on damp microfiber cloth and wipe down face of locker door. 4. Wipe dry with clean cloth. | CUST_JANITOR
CS-OUTRAIL-001M | 1. Get a spray bottle and fill with an approved disinfectant solution. 2. Spray disinfectant solution on handrails and support rails. 3. Wipe with dry cleaning cloth. 4. Ensure that all dirt, dust, and debris are removed. | CUST_JANITOR
CS-PARQFLR-001S | 1. Sweep and dust mop floor to remove all debris. 2. "Screen" entire floor area. 3. Apply the approved floor finish to restore floor. 4. Let dry. | CUST_JANITOR
CS-QCINSP-001W | 1. Perform quality control inspections in accordance with the required frequencies listed for each building in Technical Exhibit 1 (column E). 2. Document findings at the end of each day by updating the Quality Control Report Templates found in Technical Exhibit 5 and attaching the file to the work request. | CUST_JANITOR
CS-RAZDRUBR-001Q | 1. Dust mop the entire area with a microfiber mop. 2. Apply the manufacturer's recommended product. Spray solution lightly (small amount). 3. Using a low-speed buffing machine and a white pad ONLY, lightly scrub floor to remove build up. 4. Remove all solution and residue with a wet/dry vac. 5. Damp mop area with a clean micorfiber mop and manufacturer recommended cleaning solution. 6. Ensure floor is free of streaks and residue. | CUST_JANITOR
CS-RAZDRUBR-001S | 1. Dust mop the entire area with a microfiber mop. 2. Apply the manufacturer's recommended product. Spray solution lightly (small amount). 3. Using a low-speed buffing machine and a white pad ONLY, lightly scrub floor to remove build up. 4. Remove all solution and residue with a wet/dry vac. 5. Damp mop area with a clean micorfiber mop and manufacturer recommended cleaning solution. 6. Ensure floor is free of streaks and residue. | CUST_JANITOR
CS-ROOM-001W | 1. Wipe tables, chairs, shelves, cabinets, and ledges with an approved cleaning solution. 2. Wipe dry with a clean cloth. 3. Polish wood with an approved polish (where applicable). 4. Vacuum floors. | CUST_JANITOR
CS-RRVENTS-001M | 1. Dust vents by removing all debris including dust, cobwebs, mildew, etc. 2. Use an approved cleaning solution and cloth to ensure proper cleaning. | CUST_JANITOR
CS-RRVENTS-001Q | 1. Dust vents by removing all debris including dust, cobwebs, mildew, etc. 2. Use an approved cleaning solution and cloth to ensure proper cleaning. | CUST_JANITOR
CS-RRVENTS-001S | 1. Dust vents by removing all debris including dust, cobwebs, mildew, etc. 2. Use an approved cleaning solution and cloth to ensure proper cleaning. | CUST_JANITOR
CS-RRWALL-001B | 1. Clean all walls (including ceramic tile, painted, stall partitions) with an approved cleaning and disinfecting solution. 2. Wipe down with a dry cloth. 3. Ensure the walls are free of streaks, debris, tape, or any foreign matter. | CUST_JANITOR
CS-RRWALL-001M | 1. Clean all walls (including ceramic tile, painted, stall partitions) with an approved cleaning and disinfecting solution. 2. Wipe down with a dry cloth. 3. Ensure the walls are free of streaks, debris, tape, or any foreign matter. | CUST_JANITOR
CS-SCRUBFLR-001M | 1. Sweep floor with ride-on floor sweeper. 2. Apply an approved cleaning solution. Use proper ventilation dependant upon solution. 3. Machine scrub the entire floor area with a low-speed machine. 4. Use wet/dry vacuum to remove solution. 5. Mop floor as many times as needed to remove all solution. 6. Ensure that the floor is free of streaks and all residue. 7. Let dry. | CUST_JANITOR
CS-SCRUBFLR-001Q | 1. Sweep floor. 2. Apply an approved cleaning solution. Use proper ventilation dependant upon solution. 3. Machine scrub the entire floor area with a low-speed machine. 4. Use wet/dry vacuum to remove solution. 5. Mop floor as many times as needed to remove all solution. 6. Ensure that the floor is free of streaks and all residue. 7. Let dry. | CUST_JANITOR
CS-SCRUBFLR-001S | 1. Sweep floor with ride-on floor sweeper. 2. Apply an approved cleaning solution. Use proper ventilation dependant upon solution. 3. Machine scrub the entire floor area with a ride on floor scrubbing machine. 4. Ensure that the floor is free of all residue. 5. Let dry. | CUST_JANITOR
CS-SCRUBFLR-001W | 1. Sweep floor. 2. Apply an approved cleaning solution. Use proper ventilation dependant upon solution. 3. Machine scrub the entire floor area with a low-speed machine. 4. Use wet/dry vacuum to remove solution. 5. Mop floor as many times as needed to remove all solution. 6. Ensure that the floor is free of streaks and all residue. 7. Let dry. | CUST_JANITOR
CS-SCRUBFLR-002M | 1. Close off the work area. 2. Sweep the floor. 3. With approved floor cleaner scrub the floor surface with a mop/sponge/ microfiber cloth. 4. Ensure the floor is dry and reopen the area | CUST_JANITOR
CS-SCRUBFLR-002S | 1. Close off the work area. 2. Sweep the floor. 3. With approved floor cleaner scrub the floor surface with a mop/sponge/ microfiber cloth. 4. Ensure the floor is dry and reopen the area | CUST_JANITOR
CS-SHAMPOO-001A | 1. Vacuum carpet. 2. Apply approved carpet cleaning solution. 3. Use rotary scrub machine to clean. 4. Let Dry. 5. Vacuum to remove any powder residue. | CUST_JANITOR
CS-SHAMPOO-001Q | 1. Vacuum carpet. 2. Apply approved carpet cleaning solution. 3. Use rotary scrub machine to clean. 4. Let Dry. 5. Vacuum to remove any powder residue. | CUST_JANITOR
CS-SHAMPOO-001S | 1. Vacuum carpet. 2. Apply approved low-moisture carpet cleaning solution. 3. Use rotary scrub machine to clean. 4. Let Dry. 5. Vacuum carpet to remove any powder residue. | CUST_JANITOR
CS-SHOWER-001M | 1. Apply approved cleaning solution to shower walls and floors and wait 5 minutes. 2. Scrub entire shower. 3. Rinse. | CUST_JANITOR
CS-SHOWER-001W | 1. Apply approved cleaning solution to shower walls and floors and wait 5 minutes. 2. Scrub entire shower. 3. Rinse. | CUST_JANITOR
CS-STRIPWAX-001A | 1. Dust mop entire floor. 2. Apply stripper in sections (e.g., section 10' x 10'). 3. Let stripper stand for 10 minutes. 4. Machine scrub with a low speed (175-300RPM) machine scrub and the appropriate pad.,(White) 5. Wet vac entire area. 6. Mop and mop to remove all stripper and residue. Change water often to ensure a clean floor. 7. Mop again to ensure no contamination. 8. Let floor dry completely. 9. Get the wax bucket, cover with plastic, and fill with approved wax/finish. 10. Apply wax/finish and let dry. 11. Apply several coats depending on floor and allowing proper drying time between each application. 12. Let entire floor cure 48 hours before any buffing can be performed on the floor. 13. Return after floor is cured and machine buff waxed flooron low speed 175-300 RPM to high shine | CUST_JANITOR
CS-STRIPWAX-002A | 1. Dust mop entire floor. 2. Apply stripper in sections 3. Let stripper stand for 10 minutes. 4. Machine scrub landings on the lowest setting between 175-300 rpm and the appropriate pad,(white). 5. Hand scrub each individual stair. 6. Wet vac entire area. 7. Mop and mop to remove all stripper and residue. Change water often to ensure a clean floor. 8. Mop again to ensure no contamination. 9. Let floor dry completely. 10. Wipe down all stair risers and baseboards to remove any residue. 11. Get the wax bucket, cover with plastic, and fill with approved wax/finish. 12. Apply wax/finish and let dry. 13. Apply several coats depending on floor and allowing proper drying time between each application. 14. Let entire floor cure 48 hours before any buffing can be performed on the floor. 15. Return after floor is cured and machine buff waxed floor on low speed 175-300 RPM to high shine | CUST_JANITOR
CS-SWEEPCON-001W | Services are to be performed on loading dock area and adjacent hallway (if applicable). 1. Broom sweep entire concrete floor to remove all debris. | CUST_JANITOR
CS-TOWERW-001B | 1. Wash the outside of the Tower windows using an approved window cleaning solution and squeege. 2. Remove all dirt and grime. Rinse with clear water and dry with squeegee. 3. Repeat for the inside of the tower windows. 4. Clean shades. | CUST_JANITOR
CS-TRASH-001W | 1. Remove trash from receptical 2. Replace receptical liner . 3. Collect any fallen debris from receptical area 4. Remove all trash from the area and take to trash collection point.. | CUST_JANITOR
CS-URINAL-001W | 1. Remove and clean the urinal strainer. 2. Pour 2 gallons of water directly into the drain. 3. Pour 1 ounce of waterless urinal cleaner directly into the drain. 4. Allow to stand for 10 Minutes. 5. Pour 2 gallons of water into the drain as quickly as possible. - Do not let it overflow. 6. Pour in 3 ounces of waterless urinal sealing liquid. 7. Re-install the strainer. 8. Add one (1) cap full of enzymatic deodorizer. | CUST_JANITOR
CS-URINALC-001S | 1. Insert Sloan Key into the cartridge, turn left to unlock. Pull the cartridge loose,tilt to drain liquids and discard the old cartridge into a sealed bag and dispose. 2. Scrub the housing and deep inside the tailpipe with a long 1.5 inch diameter nylon brush. 3. Flush the housing with 5 gallons hot soapy water. 4. Wipe clean the inner steele rim. 5. Insert the new cartridge and turn right to lock and click into place. 6. Slowly fill the cartridge with 1 quart (1Liter) of or more of clean water until there are no air bubbles. 7. Add Blue sealant (allow time time to drain into cartridge). 8. Spray (mist) cleaner and wipe the urinal clean. | CUST_JANITOR
CS-URNLDEOD-001W | 1. Add one (1) cap full of enzymatic deodorizer or as per manufacture's instructions. | CUST_JANITOR
CS-URNLDMAT-001B | 1. Change scented urinal deodorizing mat in urinals | CUST_JANITOR
CS-URNLDMAT-001M | 1. Change scented urinal deodorizing mat in urinals | CUST_JANITOR
CS-VACSTAIR-001M | 1. Vacuum entire stairs/stairwells to remove all debris from steps and landings. | CUST_JANITOR
CS-VACSTAIR-001W | 1. Vacuum entire stairs/stairwells to remove all debris from steps and landings. | CUST_JANITOR
CS-WALOUTLB-001Q | 1. Spray wall with an approved cleaner. 2. Wipe down all walls to remove and debris, spot, residue or trace material. | CUST_JANITOR
CS-WINDOSIL-001Q | 1. Remove all dust, cobwebs, debris etc. from surfaces. 2. Apply approved cleaning solution to cloth and wipe down surfaces. | CUST_JANITOR
CS-WINDOW-001A | 1. Wash the windows using an approved window cleaning solution and squeegee. 2. Remove all dirt and grime. 3. Rinse with clear water and dry with squeegee. 4. Clean sills, ledges and all areas beneath the windows. | CUST_JANITOR
GR-FENCE-001M | 1. Assess fence line 2. Trim if required | GROUNDS
GR-IRRIGATE-001A | 1. Charge irrigation systems 2. Test zones 3. Make repairs if necessary | GROUNDS
GR-IRRIGATE-002A | 1. Winterize and blow out irrigation systems | GROUNDS
GR-PLANTING-001A | 1. Clean and prep beds 2. Plant flowers | GROUNDS
GR-PLANTING-002A | 1. Clean and prep beds 2. Plant flowers | GROUNDS
GR-PLANTING-003A | 1. Clean and prep beds 2. Plant flowers | GROUNDS
GR-POLICING-001M | 1. Assess facility 2. Police areas as needed | GROUNDS
GR-WEEDS-001M | 1. Assess weeds throughout facility 2. Spray if required 3. Record chemical and amounts used | GROUNDS
DRAFT